## Modeling Data (Rev 6) (hidden)
| 1 - Lighting |  |  |  | 2 - Plug Loads |  |  |  |  | 3 - Occupancy |  |  |  | 4 - Outdoor Air |  | 5 - Water Heating |  | 6 - Process |  | 7 - Schedules
| Allowed Lighting Power Density (W/ft²) |  |  |  | Default Receptacle Power Density (W/ft²) |  | Receptacle Power Coefficients |  |  | Occupant Density (ft³/person) |  | Heat Gain per Occupant (Btu/occ) |  | Minimum Ventilation (cfm/ft²) |  | Load (Btu/h-occ) | Load (G/day-occ) | Interior Gas Appliance Power Density (Btu/h-ft²) | Refrigeration Power Density (W/ft²)
| ASHRAE Standard 90.1-2001 | ASHRAE Standard 90.1-2007 | ASHRAE Standard 90.1-2010 | Room Cavity Ratio Threshold | California 2005 ACM | COMNET | Csd | PDmisc | D | California 2005 ACM | COMNET | Sensible | Latent | California 2005 ACM | COMNET | California 2005 ACM | COMNET |  |  | California 2005 Schedule | COMNET Schedule
Whole Building Categories
Auto Repair | 1.5 | 0.9 | 0.82 | n.a. | 1 | 0.6 | 2 | 0.54813 | 0.943 | 142.8571 | 143 | 375 | 625 | 0.15 | 0.15 | 120 | 1.004 | 0.75064 | 0.12 | Non-Residential | Table G-H Light Manufacturing Occupancy
Convention Center | 1.4 | 1.2 | 1.08 | n.a. | 0.96 | 0.9 | 2 | 0.54813 | 0.779 | 7.3529 | 9 | 245 | 112 | 1.02 | 1.02 | 57 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Court House | 1.4 | 1.2 | 1.05 | n.a. | 1 | 0.9 | 2 | 0.54813 | 0.923 | 6.993 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Dining, Bar/Cocktail Lounge | 1.5 | 1.3 | 0.99 | n.a. | 0.79 | 1.4 | 2 | 0.92903 | 1 | 22.2222 | 30 | 274 | 334 | 0.38 | 0.38 | 366 | 10.0396 | 17.5377 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Cafeteria/Fast Food | 1.8 | 1.4 | 0.9 | n.a. | 0.79 | 1.4 | 2 | 0.92903 | 1 | 22.2222 | 30 | 274 | 334 | 0.38 | 0.38 | 366 | 10.0396 | 17.5377 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Family | 1.9 | 1.6 | 0.89 | n.a. | 0.79 | 1.4 | 2 | 0.92903 | 1 | 22.2222 | 30 | 274 | 334 | 0.38 | 0.38 | 366 | 10.0396 | 17.5377 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Dormitory | 1.5 | 1 | 0.61 | n.a. | 0.5 | 0.9 | 2 | 0.29729 | 0.565 | 50 | 150 | 255 | 875 | 0.15 | N/A | 120 | Note 1 | 0.6824 | 0.14 | Residential | Table G-G Hotel/Motel Occupancy
Exercise Center | 1.4 | 1 | 0.88 | n.a. | 1 | 1.6 | 2 | 0.54813 | 0.779 | 100 | 50 | 250 | 200 | 0.15 | 0.15 | 120 | 1.004 | 0.30708 | 0.1 | Non-Residential | Table G-E Assembly Occupancy
Fire Station | 1.3 | 1 | 0.71 | n.a. | 1.5 | 1.7 | 2 | 1.1148 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 1 | 0.31 | 0.06 | Non-Residential | Table G-I Office Occupancy
Gymnasium | 1.7 | 1.1 | 1 | n.a. | 1 | 1.6 | 2 | 0.54813 | 0.779 | 100 | 50 | 250 | 200 | 0.15 | 0.15 | 120 | 1.004 | 0.30708 | 0.1 | Non-Residential | Table G-E Assembly Occupancy
Health Care Clinic | 1.6 | 1 | 0.87 | n.a. | 1.18 | 1.5 | 2 | 0.76181 | 0.962 | 100 | 100 | 250 | 213 | 0.15 | 0.15 | 110 | 3.0119 | 1.126 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital | 1.6 | 1.2 | 1.21 | n.a. | 1.18 | 1.5 | 2 | 0.76181 | 0.68 | 100 | 100 | 250 | 213 | 0.15 | 0.15 | 110 | 3.0119 | 1.126 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hotel | 1.7 | 1 | 1 | n.a. | 1.5 | 0.9 | 2 | 0.29729 | 0.565 | 100 | 200 | 250 | 200 | 0.15 | N/A | 160 | Note 1 | 0.6824 | 0.14 | Hotel Function | Table G-G Hotel/Motel Occupancy
Library | 1.5 | 1.3 | 1.18 | n.a. | 1.5 | 1.1 | 2 | 0.18581 | 0.779 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 0.18 | 0.13648 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Manufacturing Facility | 2.2 | 1.3 | 1.11 | n.a. | 1 | 0.4 | 2 | 0.18581 | 1 | 142.8571 | 200 | 375 | 625 | 0.15 | 0.15 | 120 | 0.60766 | 0 | 0.05 | Non-Residential | Table G-H Light Manufacturing Occupancy
Motel | 2 | 1 | 0.88 | n.a. | 1.5 | 0.9 | 2 | 0.29729 | 0.565 | 100 | 200 | 250 | 200 | 0.15 | N/A | 160 | Note 1 | 0.6824 | 0.14 | Residential | Table G-G Hotel/Motel Occupancy
Motion Picture Theatre | 1.6 | 1.2 | 0.83 | n.a. | 0.54 | 0.9 | 2 | 0.54813 | 0.779 | 7.6923 | 9 | 268 | 403 | 0.98 | 0.98 | 60 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Multi-Family | 1 | 0.7 | 0.6 | n.a. | 1.5 | 1.6 | 2 | 0.92894 | 1 | 200 | 200 | 275 | 475 | 0.15 | 0.15 | 385 | Note 2 | 0.30708 | 0.1 | Residential | Table G-G Hotel/Motel Occupancy
Museum- General | 1.6 | 1.1 | 1.06 | n.a. | 1 | 0.9 | 2 | 0.54813 | 0.779 | 142.8571 | 50 | 375 | 625 | 0.15 | 0.15 | 120 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Office | 1.3 | 1 | 0.9 | n.a. | 1.34 | 2.2 | 2 | 0.7711 | 0.923 | 100 | 150 | 250 | 206 | 0.15 | 0.15 | 106 | 1.004 | 0.13648 | 0.06 | Non-Residential | Table G-I Office Occupancy
Parking Garage | 0.3 | 0.3 | 0.25 | n.a. | 1 | 0.6 | 2 | 0.54813 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 0 | 0 | 0 | Retail | Table G-J Parking Garage Occupancy
Penitentiary | 1.2 | 1 | 0.97 | n.a. | 1.5 | 0.9 | 2 | 0.29729 | 0.565 | 200 | 250 | 275 | 475 | 0.15 | 0.15 | 385 | Note 1 | 0.6824 | 0.14 | Residential | Table G-E Assembly Occupancy
Performing Arts Theatre | 1.5 | 1.6 | 1.36 | n.a. | 0.54 | 0.9 | 2 | 0.54813 | 0.779 | 7.6923 | 9 | 268 | 403 | 0.98 | 0.98 | 60 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Police Station | 1.3 | 1 | 0.96 | n.a. | 1.34 | 1.7 | 2 | 1.1148 | 0.627 | 100 | 100 | 250 | 206 | 0.15 | 0.15 | 106 | 1.004 | 0.30708 | 0.06 | Non-Residential | Table G-I Office Occupancy
Post Office | 1.6 | 1.1 | 0.87 | n.a. | 1 | 2.2 | 2 | 0.7711 | 0.963 | 142.8571 | 100 | 375 | 625 | 0.15 | 0.15 | 120 | 1.004 | 0.13648 | 0.07 | Non-Residential | Table G-I Office Occupancy
Religious Building | 2.2 | 1.3 | 1.05 | n.a. | 0.96 | 0.3 | 2 | 0.54813 | 0.972 | 7.3529 | 9 | 245 | 112 | 1.03 | 1.03 | 57 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Retail | 1.9 | 1.5 | 1.4 | n.a. | 1.5 | 0.7 | 2 | 0.34374 | 0.963 | 100 | 100 | 250 | 250 | 0.15 | N/A | 0 | 0.60766 | 0.10236 | 0.15 | Retail | Table G-L Retail Occupancy
School/University | 1.5 | 1.2 | 0.99 | n.a. | 1 | 1.1 | 2 | N/A | 0.773 | 25 | 50 | 246 | 171 | 0.32 | 0.32 | 108 | 0.60766 | 0.30708 | 0.1 | Non-Residential | Table G-M School Occupancy
Sports Arena | 1.5 | 1.1 | 0.78 | n.a. | 1 | 0.9 | 2 | 0.54813 | 0.779 | 6.993 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Town Hall | 1.4 | 1.1 | 0.92 | n.a. | 1 | 0.9 | 2 | 0.54813 | 0.779 | 6.993 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.2642 | 0.13648 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transportation | 1.2 | 1 | 0.77 | n.a. | 1 | 1.6 | 2 | 0.54813 | 0.839 | 100 | 60 | 250 | 200 | 0.15 | 0.15 | 120 | 1.004 | 0.30708 | 0.1 | Non-Residential | Table G-E Assembly Occupancy
Warehouse | 1.2 | 0.8 | 0.66 | n.a. | 1 | 0.4 | 2 | 0.18581 | 1 | 142.8571 | 333 | 375 | 625 | 0.15 | 0.15 | 120 | 0.60766 | 0 | 0.05 | Non-Residential | Table G-N Warehouse Occupancy
Workshop | 1.7 | 1.4 | 1.2 | n.a. | 1 | 0.4 | 2 | 0.18581 | 0.943 | 142.8571 | 200 | 375 | 625 | 0.15 | 0.15 | 120 | 0.60766 | 0 | 0.05 | Non-Residential | Table G-H Light Manufacturing Occupancy
Space-by-Space Classifications
Atrium,(First 40 ft in height) | 1.3 | 0.6 | 0.03 (watts per ft height) | n.a.
Atrium,(Height above 40 ft ) | 0.2 | 0.2 | 0.02 (watts per ft height) | n.a.
Audience/Seating Area, Permanent for Auditorium | 3.2 | 1.7 | 0.79 | 6 | 1 | 0.90752 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Audience/Seating Area, Permanent for Motion Picture Theater | 1.3 | 1.2 | 2.43 | 8 | 1 | 0.90752 | 2 | 0.54807 | 1 | 333 | 5000 | 275 | 475 | 0.15 | 0.15 | 120 | 0 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Audience/Seating Area, Permanent for Performing Arts Theater | 1.8 | 2.6 | 1.14 | 4 | 1 | 0.90752 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Automotive,Service/Repair | 1.4 | 0.7 | 0.67 | 4 | 1 | 0.64828 | 2 | 0.54807 | 1 | 100 | 100 | 275 | 475 | 1.5 | 1.5 | 120 | 1 | 0.75 | 0.12 | Non-Residential | Table G-H Light Manufacturing Occupancy
Bank/Office,Banking Activity Area | 2.4 | 1.5 | 1.38 | 6 | 1.5 | 2.309 | 2 | 0.77102 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 1 | 0.14 | 0.06 | Non-Residential | Table G-I Office Occupancy
Classroom/Lecture/Training | 1.6 | 1.4 | 1.24 | 4 | 1 | 0.92841 | 2 | 0.14863 | 1 | 20 | 20 | 245 | 155 | 0.38 | 0.38 | 120 | Note 3 | 0.14 | 0.06 | Non-Residential | Table G-M School Occupancy
Conference/Meeting/Multipurpose | 1.5 | 1.3 | 1.23 | 6 | 1 | 0.78836 | 2 | 0.54807 | 1 | 15 | 15 | 245 | 155 | 0.5 | 0.5 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Convention Center, Audience Seating | 0.5 | 0.7 | 0.82 | 4 | 1 | 0.90752 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Convention Center, Exhibit Space | 0.8 | 0.6 | 1.45 | 4 | 1 | 0.90752 | 2 | 0.54807 | 1 | 15 | 30 | 245 | 155 | 0.15 | 0.15 | 385 | N/A | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Corridor/Transition | 0.7 | 0.5 | 0.66 | Width<8 ft | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 100 | 200 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Courthouse/Police Station/Penitentiary, Confinement Cells | 1.1 | 0.9 | 1.1 | 6 | 0.2 | 1.7354 | 2 | 1.1147 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 0 | 1 | 0.31 | 0.06 | Residential | Table G-E Assembly Occupancy
Courthouse/Police Station/Penitentiary, Courtroom | 2.1 | 1.9 | 1.72 | 6 | 1.5 | 1.7354 | 2 | 1.1147 | 1 | 40 | 40 | 250 | 200 | 0.19 | 0.19 | 120 | 1 | 0.31 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Courthouse/Police Station/Penitentiary, Judges’ Chambers | 1.1 | 1.3 | 1.17 | 8 | 1.5 | 2.3111 | 2 | 0.77102 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 1 | 0.14 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Dining Area, General | 1.4 | 0.9 | 0.65 | 4 | 0.5 | 1.3449 | 2 | 0.92894 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 385 | 10.04 | 17.54 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Dining Area, Bar Lounge/Leisure Dining | 1.2 | 1.4 | 1.31 | 4 | 1 | 1.3449 | 2 | 0.92894 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 120 | 10.04 | 17.54 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Dining Area, Family Dining | 2.2 | 2.1 | 0.89 | 4 | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 385 | 10.04 | 0 | 0 | Non-Residential | Table G-K Restaurant Occupancy
Dormitory, Living Quarters | 1.9 | 1.1 | 0.38 | 8 | 0.5 | 1.4392 | 2 | 0.29726 | 1 | 100 | 150 | 250 | 250 | 0.15 | 0.15 | 120 | Note 1 | 0.68 | 0.14 | Residential | Table G-G Hotel/Motel Occupancy
Dressing/Fitting Room , Performing Arts Theater | N/A | N/A | 0.4 | 6 | 0.5 | 1.5796 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 385 | N/A | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Electrical/Mechanical | 0.8 | 0.6 | 0.95 | 6 | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 333 | 750 | 250 | 250 | 0.15 | 0.15 | 385 | N/A | 0 | 0 | Non-Residential | Table G-H Light Manufacturing Occupancy
Equipment Room | 0.8 | 0.6 | 0.95 | 6 | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 333 | 750 | 250 | 250 | 0.15 | 0.15 | 385 | N/A | 0 | 0 | Non-Residential | Table G-H Light Manufacturing Occupancy
Fire Stations, Engine Room | 0.9 | 0.8 | 0.56 | 4 | 1.5 | 1.7055 | 2 | 1.1147 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 1 | 0.31 | 0.06 | Non-Residential | Table G-I Office Occupancy
Fire Stations, Sleeping Quarters | 1.1 | 0.3 | 0.25 | 6 | 0.5 | 1.7055 | 2 | 1.1147 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Residential | Table G-I Office Occupancy
Food Preparation | 2.2 | 1.2 | 0.99 | 6 | 1.5 | 1.4196 | 2 | 0.92894 | 1 | 200 | 200 | 275 | 475 | 0.15 | 0.15 | 385 | 10.04 | 17.54 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Gymnasium/Fitness Center, Fitness Area | 1.1 | 0.9 | 0.72 | 4 | 0.5 | 0.71678 | 2 | 0.54807 | 1 | 50 | 50 | 255 | 875 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-E Assembly Occupancy
Gymnasium/Fitness Center, Gymnasium Audience Seating | 1.1 | 0.9 | 0.43 | 6 | 0.5 | 0.71678 | 2 | 0.54807 | 1 | 50 | 50 | 255 | 875 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-E Assembly Occupancy
Gymnasium/Fitness Center, Playing Area | 1.9 | 1.4 | 1.2 | 4 | 0.5 | 0.71678 | 2 | 0.54807 | 1 | 50 | 50 | 255 | 875 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-E Assembly Occupancy
Home Nursing/Senior Housing | 2.5 | 1.1 | 1.11 | 6 | 0.5 | 1.4839 | 2 | 1.1147 | 1 | 100 | 200 | 250 | 250 | 0.15 | 0.15 | 120 | 3.01 | 1.13 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Hospital, Corridor/Transition | 1.6 | 1 | 0.89 | Width < 8 ft | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | Non-Residential | Table G-F Health Occupancy
Hospital, Emergency | 2.8 | 2.7 | 2.26 | 6 | 1.5 | 1.5463 | 2 | 0.76173 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Exam/Treatment | 1.6 | 1.5 | 1.66 | 8 | 1.5 | 1.5642 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Laundry/Washing | 2.5 | 1.1 | 0.6 | 4 | 3 | 0.65444 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 2800 | Note 1 | 0.75 | 0.12 | Residential | Table G-F Health Occupancy
Hospital, Lounge/Recreation | 1.6 | 1.5 | 1.07 | 6 | 0.5 | 0.71678 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 0.14 | 0.03 | Non-Residential | Table G-F Health Occupancy
Hospital, Medical Supply | 3 | 1.4 | 1.27 | 6 | 1.5 | 1.5463 | 2 | 0.76173 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Nursery | 1 | 0.6 | 0.88 | 6 | 0.5 | 1.4839 | 2 | 1.1147 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Nurses’ Station | 1.8 | 1 | 0.87 | 6 | 1.5 | 1.5642 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Operating Room | 7.6 | 2.2 | 1.89 | 6 | 1.5 | 1.5463 | 2 | 0.76173 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Patient Room | 1.2 | 0.7 | 0.62 | 6 | 0.5 | 1.4839 | 2 | 1.1147 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | N/A | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Pharmacy | 2.3 | 1.2 | 1.14 | 6 | 1.5 | 1.5642 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Physical Therapy | 2.3 | 1.2 | 0.91 | 6 | 1.5 | 1.5463 | 2 | 0.76173 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Radiology/Imaging | 0.4 | 0.4 | 1.32 | 6 | 1.5 | 1.5463 | 2 | 0.76173 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hospital, Recovery | 2.6 | 0.8 | 1.15 | 6 | 1.5 | 1.5463 | 2 | 0.76173 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 3.01 | 1.13 | 0.08 | Non-Residential | Table G-F Health Occupancy
Hotel Dining | 1 | 1.3 | 0.82 | 4 | 0.5 | 1.3449 | 2 | 0.92894 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 385 | 10.04 | 17.54 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Hotel Guest Rooms | 2.5 | 1.1 | 1.11 | 6 | 0.5 | 0.82458 | 2 | 0.29726 | 1 | 200 | 200 | 245 | 155 | 0.15 | 0.15 | 2800 | Note 1 | 0.68 | 0.14 | Residential | Table G-G Hotel/Motel Occupancy
Hotel Lobby | 1.7 | 1.1 | 1.06 | 4 | 0.5 | 0.82458 | 2 | 0.29726 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 0 | 0.68 | 0.14 | Residential | Table G-G Hotel/Motel Occupancy
Highway Lodging Dining | 1.2 | 1.2 | 0.88 | 4 | 0.5 | 1.3449 | 2 | 0.92894 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 385 | 10.04 | 17.54 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Highway Lodging Guest Rooms | 3 | 1.4 | 0.75 | 6 | 0.5 | 0.82458 | 2 | 0.29726 | 1 | 200 | 200 | 245 | 155 | 0.15 | 0.15 | 160 | 3.01 | 0.68 | 0.14 | Non-Residential | Table G-G Hotel/Motel Occupancy
Laboratory, Classrooms | 2.5 | 1.1 | 1.28 | 6 | 1 | 3.639 | 2 | 2.7868 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 2800 | Note 1 | 12.69 | 0.28 | Residential | Table G-G Hotel/Motel Occupancy
Laboratory, Medical/Industrial/Research | 2.5 | 1.1 | 1.81 | 6 | 1 | 3.639 | 2 | 2.7868 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 2800 | Note 1 | 12.69 | 0.28 | Residential | Table G-G Hotel/Motel Occupancy
Laundry Facility | 2.5 | 1.1 | 0.6 | 4 | 3 | 0.65444 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 2800 | Note 1 | 0.75 | 0.12 | Residential | Table G-G Hotel/Motel Occupancy
Library, Card File and Cataloging | 1.4 | 1.1 | 0.72 | 4 | 1.5 | 1.2323 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | Note 3 | 0.14 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Library, Reading Area | 1.8 | 1.2 | 0.93 | 4 | 1.5 | 1.2323 | 2 | 0.54807 | 1 | 50 | 50 | 250 | 200 | 0.15 | 0.15 | 120 | Note 3 | 0.14 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Library, Stacks | 1.9 | 1.7 | 1.71 | 4 | 1.5 | 1.2323 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | Note 3 | 0.14 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Lobby, General | 1.8 | 1.3 | 0.9 | 4 | 0.5 | 0.82458 | 2 | 0.29726 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | N/A | 0.68 | 0.14 | Non-Residential | Table G-E Assembly Occupancy
Lobby, Elevator | 1.8 | 1.3 | 0.64 | 6 | 0.5 | 0.82458 | 2 | 0.29726 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | N/A | 0.68 | 0.14 | Non-Residential | Table G-E Assembly Occupancy
Lobby, Motion Picture Theater | 0.8 | 1.1 | 2 | 6 | 0.5 | 0.87943 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Lobby, Performing Arts Theater | 1.2 | 3.3 | 0.52 | 4 | 0.5 | 0.87943 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Locker Room | 1.2 | 3.3 | 0.75 | 6 | 0.5 | 1.5796 | 2 | 0.54807 | 1 | 50 | 50 | 255 | 475 | 0.15 | 0.15 | 60 | 0.26 | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Lounge/Recreation | 1.4 | 1.2 | 0.73 | 4 | 1 | 0.71678 | 2 | 0.54807 | 1 | 15 | 100 | 275 | 275 | 0.5 | 0.5 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Mechanical Control Room | 0.5 | 0.5 | 0.95 | 6 | 0.2 | 0.21918 | 2 | 0.092894 | 1 | 333 | 750 | 250 | 250 | 0.15 | 0.15 | 0 | N/A | 0.31 | 0.1 | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Corridor/Transition | 0.5 | 0.5 | 0.41 | Width < 8 ft | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 100 | 200 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Detailed Manufacturing | 6.2 | 2.1 | 1.29 | 4 | 1 | 0.21918 | 2 | 0.092894 | 1 | 100 | 200 | 250 | 200 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Equipment Room | 0.8 | 1.2 | 0.95 | 6 | 0.2 | 0.58801 | 2 | 0.54807 | 1 | 333 | 750 | 250 | 250 | 0.15 | 0.15 | 0 | N/A | 0.31 | 0.1 | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Extra High Bay (>50 ft Floor to Ceiling Height) | 3 | 1.7 | 1.05 | 4 | 1 | 0.21918 | 2 | 0.092894 | 1 | 100 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, High Bay (25–50 ft Floor to Ceiling Height) | 3 | 1.7 | 1.23 | 4 | 1 | 0.21918 | 2 | 0.092894 | 1 | 100 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Low Bay (<25 ft Floor to Ceiling Height) | 2.1 | 1.2 | 1.19 | 4 | 1 | 0.21918 | 2 | 0.092894 | 1 | 100 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | N/A | 0.31 | 0.1 | Non-Residential | Table G-H Light Manufacturing Occupancy
Museum, General Exhibition | 1.6 | 1 | 1.05 | 6 | 0.2 | 0.87943 | 2 | 0.54807 | 1 | 333 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | 3.01 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Museum, Restoration | 2.5 | 1.7 | 1.02 | 6 | 1.5 | 0.84349 | 2 | 0.18579 | 1 | 15 | 30 | 250 | 250 | 0.5 | 0.5 | 60 | 0.26 | 0.14 | 0.06 | Non-Residential | Table G-E Assembly Occupancy
Storage, Active, Musuem | 1.4 | N/A | 0.63 | 6 | 0.2 | 0.22665 | 2 | 0.18579 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Storage, Inactive, Musuem | 1.4 | 0.8 | 0.63 | 6 | 0.2 | 0.22665 | 2 | 0.18579 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Office, Enclosed | 1.5 | 1.1 | 1.11 | 8 | 1.5 | 2.3015 | 2 | 0.77102 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 1 | 0.14 | 0.07 | Non-Residential | Table G-I Office Occupancy
Office, Open Plan | 1.3 | 1.1 | 0.98 | 4 | 1.5 | 2.1656 | 2 | 0.77102 | 1 | 100 | 150 | 250 | 200 | 0.15 | 0.15 | 120 | 1 | 0.14 | 0.06 | Non-Residential | Table G-I Office Occupancy
Parking Garage, Garage Area | 0.2 | 0.2 | 0.19 | 4 | 1.5 | 0.58801 | 2 | 0.54807 | 1 | 100 | N/A | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | Non-Residential | Table G-J Parking Garage Occupancy
Penitentiary Audience Seating | 1.9 | 0.7 | 0.43 | 4 | 1 | 0.90752 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Penitentiary Classroom | 1.4 | 1.3 | 1.34 | 4 | 1 | 0.92841 | 2 | 0.14863 | 1 | 20 | 20 | 245 | 155 | 0.38 | 0.38 | 120 | Note 3 | 0.14 | 0.06 | Non-Residential | Table G-M School Occupancy
Penitentiary Dining | N/A | 1.3 | 1.07 | 6 | 0.5 | 1.5234 | 2 | 0.92894 | 1 | 15 | 15 | 275 | 275 | 0.5 | 0.5 | 385 | 10.04 | 17.54 | 1.12 | Non-Residential | Table G-K Restaurant Occupancy
Post Office, Sorting Area | 1.7 | 1.2 | 0.94 | 4 | 0.2 | 1.1697 | 2 | 0.54807 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0.31 | 0.1 | Non-Residential | Table G-I Office Occupancy
Religious Buildings, Audience Seating | 1.7 | 1.2 | 1.53 | 4 | 0.5 | 0.33077 | 2 | 0.54807 | 0.4 | 100 | 100 | 275 | 475 | 0.15 | 0.15 | 0 | 0 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Religious Buildings, Fellowship Hall | 2.3 | 0.9 | 0.64 | 4 | 0.5 | 0.33077 | 2 | 0.54807 | 0.4 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Religious Buildings, Worship Pulpit, Choir | 2.3 | 0.9 | 1.53 | 4 | 1 | 0.33077 | 2 | 0.54807 | 0.4 | 100 | 100 | 275 | 475 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Restrooms | 1 | 0.9 | 0.98 | 8 | 0.5 | 1.5796 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Retail Dressing/Fitting Room | 0.8 | 0.6 | 0.87 | 8 | 0.5 | 1.5796 | 2 | 0.54807 | 1 | 50 | 50 | 255 | 475 | 0.15 | 0.15 | 385 | N/A | 0 | 0 | Non-Residential | Table G-L Retail Occupancy
Retail Mall Concourse | 1.8 | 1.7 | 1.1 | 4 | 1 | 1.0088 | 2 | 0.34371 | 1 | 30 | 60 | 250 | 200 | 0.25 | 0.25 | 120 | 5.02 | 0 | 0 | Non-Residential | Table G-L Retail Occupancy
Retail Sales Area | 2.1* | 1.7 | 1.68 | 6 | 0.5 | 0.64632 | 2 | 0.34371 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | N/A | 0.1 | 0.15 | Retail | Table G-L Retail Occupancy
Sports Arena, Audience Seating | 0.5 | 0.4 | 0.43 | 4 | 1 | 0.90752 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Sports Arena, Court Sports Arena—Class 1 | 4.3 | 2.3 | 0.72 | 4 | 1 | 0.87943 | 2 | 0.54807 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 0.61 | 0.14 | 0.03 | Retail | Table G-E Assembly Occupancy
Sports Arena, Court Sports Arena—Class 2 | 4.3 | 2.3 | 1.2 | 4 | 1 | 0.87943 | 2 | 0.54807 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 0.61 | 0.14 | 0.03 | Retail | Table G-E Assembly Occupancy
Sports Arena, Court Sports Arena—Class 3 | 4.3 | 2.3 | 1.92 | 4 | 1 | 0.87943 | 2 | 0.54807 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 0.61 | 0.14 | 0.03 | Retail | Table G-E Assembly Occupancy
Sports Arena, Court Sports Arena—Class 4 | 4.3 | 2.3 | 3.01 | 4 | 1 | 0.87943 | 2 | 0.54807 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 0.61 | 0.14 | 0.03 | Retail | Table G-E Assembly Occupancy
Sports Arena, Indoor Sports Fields | 1.9 | 1.4 | 0.72 | 4 | 1 | 0.87943 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Sports Arena, Ring Sports Arena | 3.8 | 2.7 | 2.68 | 4 | 1 | 0.87943 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Stairway | 0.9 | 0.6 | 0.69 | 10 | 1 | 0.58801 | 2 | 0.54807 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 0.26 | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Storage, Inactive, General | 0.3 | 0.3 | 0.63 | 6 | 0.2 | 0.22665 | 2 | 0.18579 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Storage | 1.1 | 0.08 | 0.63 | 6 | 0.2 | 0.22665 | 2 | 0.18579 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Transportation, Air/Train/Bus—Baggage Area | 1.3 | 1 | 0.76 | 4 | 0.5 | 0.90752 | 2 | 0.54807 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 0.26 | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Transportation, Airport—Concourse | 0.7 | 0.6 | 0.36 | 4 | 0.5 | 0.90752 | 2 | 0.54807 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transportation, Audience Seating | 1 | 0.5 | 0.54 | 4 | 0.5 | 0.90752 | 2 | 0.54807 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 0.26 | 0.14 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transportation, Terminal—Ticket Counter | 1.8 | 1.5 | 1.08 | 4 | 0.5 | 0.90752 | 2 | 0.54807 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | N/A | 0 | 0 | Non-Residential | Table G-E Assembly Occupancy
Warehouse, Fine Material Storage | 1.6 | 1.4 | 0.95 | 6 | 0.2 | 0.36652 | 2 | 0.18579 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 0.61 | 0 | 0.05 | Non-Residential | Table G-N Warehouse Occupancy
Warehouse, Medium/Bulky Material Storage | 1.1 | 0.9 | 0.58 | 4 | 0.5 | 0.36652 | 2 | 0.18579 | 1 | 30 | 30 | 250 | 250 | 0.25 | 0.25 | 120 | N/A | 0 | 0.05 | Non-Residential | Table G-E Assembly Occupancy
Warehouse, Refrigerated | 1.6 | 1.4 | 0.58 | 4 | 0.2 | 0.22665 | 2 | 0.18579 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 0.61 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Workshop, General | 2.5 | 1.9 | 1.59 | 6 | 0.2 | 0.53254 | 2 | 0.54807 | 1 | 1000 | 500 | 275 | 475 | 0.15 | 0.15 | 0 | 0.61 | 0.75 | 0.12 | Non-Residential | Table G-N Warehouse Occupancy

## Modeling Data
| Lighting Power | [5 empty] | Automatic Lighting Controls | Plug Loads |  |  |  |  | Occupancy |  |  |  | Occupancy |  |  | Ventilation Rate | Ventilation Rate |  | Water Heating | Process |  | 8 - Schedules | Schedules
| Allowed Lighting Power Density (W/ft²) | [6 empty] | Receptacle Power Coefficients |  |  |  |  | Heat Gain per Occupant (Btu/occ) | Occupant Heat Gain (Original) |  |  | Occupant Heat Gain |  |  |  |  | California ACM 2005 |  | Interior Gas Appliance Power Density (Btu/h-ft²) | Refrigeration Power Density (W/ft²)
| ASHRAE Standard 90.1-2001 | ASHRAE Standard 90.1-2007 | ASHRAE Standard 90.1-2010 | Room Cavity Ratio Threshold | ASHRAE Standard 90.1-2016 PRM | California 2005 ACM | Occupant Sensor Power Adjustment Factors | Default Power Density (W/ft²) | Power Density from SSPC 90.1 (W/ft²) | Csd | PDmisc | D | California 2005 ACM | Default Occupant Density (ft²/person) | Sensible Heat Gain (Btu/h-person) | Latent Heat Gain (Btu/h-person) | Default Occupant Density (ft²/person) | Sensible Heat Gain (Btu/h-person) | Latent Heat Gain (Btu/h-person) | Ventilation Rate (Revised) (cfm/ft²) | Ventilation Rate (Original) (cfm/ft²) | Load (Btu/h-occ) | Load (Btu/h-occ) |  |  | California 2005 Schedule | Schedule from Appendix C | SSPC 90.1 Schedule Reference | Description
Whole Building Categories
BA Automotive Facility | 1.5 | 0.9 | 0.82 | n.a. | 0.9 | 1 | n.a. | 0.50325 | 1 | 2 | 0.54833 | 1 | 100 | 200 | 275 | 475 | 143 | 375 | 625 | 0.25 | 1.5 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
BA Convention Center | 1.4 | 1.2 | 1.08 | n.a. | 1.2 | 0.96 | n.a. | 0.74761 | 0.25 | 2 | 0.54833 | 1 | 7.3529 | 50 | 245 | 112 | 20 | 250 | 200 | 0.31 | 0.3 | 57 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Courthouse | 1.4 | 1.2 | 1.05 | n.a. | 1.2 | 0.96 | n.a. | 1.669 | 0.25 | 2 | 0.77138 | 1 | 7.3529 | 200 | 245 | 112 | 14 | 250 | 200 | 0.41 | 0.4 | 57 | 135 | 0.17123 | 0.046804 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
BA Dining: Bar Lounge/Leisure | 1.5 | 1.3 | 0.99 | n.a. | 1.3 | 0.79 | n.a. | 1.3161 | 6 | 2 | 0.92937 | 1 | 22.2222 | 100 | 274 | 334 | 10 | 275 | 275 | 0.93 | 0.25 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
BA Dining: Cafeteria/Fast Food | 1.8 | 1.4 | 0.9 | n.a. | 1.4 | 0.79 | n.a. | 1.3684 | 6 | 2 | 0.92937 | 1 | 22.2222 | 100 | 274 | 334 | 10 | 275 | 275 | 0.93 | 0.25 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
BA Dining: Family | 1.9 | 1.6 | 0.89 | n.a. | 1.6 | 0.79 | n.a. | 1.263 | 6 | 2 | 0.92937 | 1 | 22.2222 | 100 | 274 | 334 | 14 | 275 | 275 | 0.71 | 0.25 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
BA Dormitory | 1.5 | 1 | 0.61 | n.a. | 1 | 0.5 | n.a. | 1.9561 | 0.6 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 100 | 250 | 200 | 0.11 | 0.05 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | C-12 Residential | F | Dormatory, multifamily
BA Exercise Center | 1.4 | 1 | 0.88 | n.a. | 1 | 1 | n.a. | 0.67425 | 0.5 | 2 | 0.54833 | 1 | 100 | 200 | 250 | 200 | 100 | 710 | 1090 | 0.26 | 0.4 | 120 | 135 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Fire Station | 1.3 | 1 | 0.71 | n.a. | 1 | 1.5 | n.a. | 1.5404 | 1.5 | 2 | 1.1152 | 1 | 100 | 250 | 250 | 200 | 33 | 250 | 200 | 0.21 | 0.08 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
BA Gymnasium | 1.7 | 1.1 | 1 | n.a. | 1.1 | 0.5 | n.a. | 0.67425 | 0.5 | 2 | 0.54833 | 1 | 50 | 200 | 255 | 875 | 33 | 710 | 1090 | 0.3 | 0.4 | 120 | 135 | 0.022831 | 0.06621 | Non-Residential | C-14 Gymnasium | I | Gymnasium
BA Healthcare Clinic | 1.6 | 1 | 0.87 | n.a. | 1 | 1.18 | n.a. | 1.2202 | 2 | 2 | 0.54833 | 1 | 100 | 200 | 250 | 213 | 200 | 250 | 200 | 0.47 | 0.4 | 110 | 135 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
BA Hospital | 1.6 | 1.2 | 1.21 | n.a. | 1.2 | 1.18 | n.a. | 1.2488 | 2 | 2 | 0.76208 | 1 | 100 | 200 | 250 | 213 | 200 | 250 | 200 | 0.47 | 0.4 | 110 | 135 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
BA Hotel | 1.7 | 1 | 1 | n.a. | 1.09 | 0.5 | n.a. | 1.5641 | 1.11 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 250 | 250 | 200 | 0.08 | 0.05 | 2800 | 1700 | 0.69635 | 0.10274 | Hotel Function | C-3 Hotel Motel | D | Hotel, motel, penitentiary
BA Library | 1.5 | 1.3 | 1.18 | n.a. | 1.3 | 1.5 | n.a. | 0.93723 | 1.5 | 2 | 0.54833 | 1 | 100 | 75 | 250 | 250 | 100 | 250 | 200 | 0.11 | 0.2 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | C | Library, museum, retail
BA Manufacturing Facility | 2.2 | 1.3 | 1.11 | n.a. | 1.17 | 1 | n.a. | 0.34481 | 1 | 2 | 0.18587 | 1 | 142.8571 | 750 | 375 | 625 | 143 | 580 | 870 | 0.25 | 0.45 | 120 | 225 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
BA Motel | 2 | 1 | 0.88 | n.a. | 1.09 | 0.5 | n.a. | 1.5641 | 1.11 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 250 | 250 | 200 | 0.08 | 0.05 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | C-3 Hotel Motel | D | Hotel, motel, penitentiary
BA Motion Picture Theater | 1.6 | 1.2 | 0.83 | n.a. | 1.2 | 1 | n.a. | 0.74485 | 0.54 | 2 | 0.54833 | 1 | 6.993 | 50 | 245 | 105 | 7 | 225 | 105 | 1.19 | 0.3 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Multifamily | 1 | 0.7 | 0.6 | n.a. | 0.7 | 0.5 | n.a. | 1.4245 | 0.62 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 380 | 250 | 200 | 0.06 | 0.06 | 1700 | 1700 | 0.69635 | 0.10274 | Residential | C-12 Residential | F | Dormatory, multifamily
BA Museum | 1.6 | 1.1 | 1.06 | n.a. | 1.1 | 1.5 | n.a. | 0.74485 | 1.5 | 2 | 0.54833 | 1 | 14.9254 | 50 | 250 | 250 | 25 | 250 | 200 | 0.36 | 0.3 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | C | Library, museum, retail
BA Office | 1.3 | 1 | 0.9 | n.a. | 1 | 1.34 | n.a. | 1.6721 | 0.75 | 2 | 0.77138 | 1 | 100 | 250 | 250 | 206 | 200 | 250 | 200 | 0.09 | 0.08 | 106 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
BA Parking Garage | 0.3 | 0.3 | 0.25 | n.a. | 0.3 | 1 | n.a. | n.a. | 0 | n.a. | n.a. | n.a. | 100 | Uncond. | 250 | 200 | 0 | 250 | 200 | 0 | 0 | 120 | 0 | 0 | 0.031963 | Retail | C-6 Parking Garage | K | Parking garage
BA Penitentiary | 1.2 | 1 | 0.97 | n.a. | 1 | 0.5 | n.a. | 1.4928 | 0.5 | 2 | 1.1152 | 1 | 200 | 250 | 245 | 155 | 40 | 250 | 200 | 0.25 | 0.05 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | C-3 Hotel Motel | D | Hotel, motel, penitentiary
BA Performing Arts Theater | 1.5 | 1.6 | 1.36 | n.a. | 1.6 | 0.5 | n.a. | 0.74485 | 0.5 | 2 | 0.54833 | 1 | 6.993 | 50 | 245 | 105 | 14 | 225 | 105 | 0.76 | 0.3 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Police Station | 1.3 | 1 | 0.96 | n.a. | 1 | 1.5 | n.a. | 1.5404 | 1.5 | 2 | 1.1152 | 1 | 100 | 250 | 250 | 200 | 33 | 250 | 200 | 0.21 | 0.08 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
BA Post Office | 1.6 | 1.1 | 0.87 | n.a. | 1.1 | 1 | n.a. | 0.90907 | 1 | 2 | 0.54833 | 1 | 100 | 250 | 275 | 475 | 33 | 250 | 200 | 0.21 | 0.08 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
BA Religious Building | 2.2 | 1.3 | 1.05 | n.a. | 1.3 | 0.96 | n.a. | 0.29845 | 0.96 | 2 | 0.54833 | 0.4 | 7.3529 | 50 | 245 | 112 | 8 | 245 | 155 | 0.66 | 0.3 | 57 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Retail | 1.9 | 1.5 | 1.4 | n.a. | 1.5 | 1 | n.a. | 0.70235 | 0.3 | 2 | 0.34387 | 1 | 30.303 | 300 | 250 | 200 | 67 | 250 | 200 | 0.23 | 0.2 | 120 | 135 | 0.091324 | 0.11758 | Retail | C-8 Retail | C | Library, museum, retail
BA School/University | 1.5 | 1.2 | 0.99 | n.a. | 1.2 | 1 | n.a. | 0.68748 | 1.39 | 2 | 0.1487 | 1 | 25 | 75 | 246 | 171 | 40 | 250 | 200 | 0.47 | 0.2 | 108 | 215 | 0.13699 | 0.057078 | Non-Residential | C-9 Schools | G | K-12 schools, universities
BA Sports Arena | 1.5 | 1.1 | 0.78 | n.a. | 1.1 | 1 | n.a. | 0.74761 | 1 | 2 | 0.54833 | 1 | 6.993 | 50 | 245 | 105 | 0 | 245 | 105 | 0.3 | 0.3 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Town Hall | 1.4 | 1.1 | 0.92 | n.a. | 1.1 | 1.34 | n.a. | 0.74761 | 1 | 2 | 0.54833 | 1 | 100 | 50 | 250 | 206 | 200 | 250 | 200 | 0.09 | 0.3 | 106 | 215 | 0.12557 | 0.053653 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
BA Transportation | 1.2 | 1 | 0.77 | n.a. | 1 | 0.5 | n.a. | 0.51912 | 0.5 | 2 | 0.54833 | 1 | 30.303 | 200 | 250 | 250 | 10 | 225 | 105 | 0.81 | 0.1 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
BA Warehouse | 1.2 | 0.8 | 0.66 | n.a. | 0.8 | 0.2 | n.a. | 0.30231 | 0.24 | 2 | 0.18587 | 1 | 333.3333 | 15000 | 275 | 475 | 0 | 275 | 475 | 0.06 | 0.2 | 120 | 1000 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | L | Warehouse
BA Workshop | 1.7 | 1.4 | 1.2 | n.a. | 1.4 | 1 | n.a. | 0.42834 | 1 | 2 | 0.54833 | 1 | 142.8571 | 750 | 375 | 625 | 143 | 635 | 965 | 0.25 | 0.45 | 120 | 225 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
Space-by-Space Classifications
CS Audience Seating Area, Auditorium | 1.6 | 0.9 | 0.79 | 6 | 0.9 | 1 | 10% | 0.74761 | 0.5 | 2 | 0.54833 | 1 | 7 | 50 | 245 | 105 | 14 | 225 | 105 | 0.76 | 0.3 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Audience Seating Area, Convention Center | 0.5 | 0.7 | 0.82 | 4 | 0.7 | 1 | 10% | 0.74761 | 0.25 | 2 | 0.54833 | 1 | 7 | 50 | 245 | 155 | 20 | 250 | 200 | 0.31 | 0.4 | 60 | 150 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Exercise Center | 0.5 | 0.3 | 0.43 | 6 | 0.3 | 1 | 10% | 0.67425 | 0.5 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 100 | 710 | 1090 | 0.26 | 0.3 | 120 | 100 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Audience Seating Area, Gymnasium | 0.5 | 0.4 | 0.43 | 6 | 0.4 | 1 | 10% | 0.67425 | 0.5 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 33 | 710 | 1090 | 0.3 | 0.3 | 120 | 100 | 0.022831 | 0.06621 |  | Use parent schedule | ps | Schedule is inherited
CS Audience Seating Area, Motion Picture Theater | 1.3 | 1.2 | 2.43 | 8 | 1.2 | 1 | 10% | 0.74485 | 0.54 | 2 | 0.54833 | 1 | 7 | 50 | 245 | 105 | 7 | 225 | 105 | 1.19 | 0.3 | 60 | 100 | 0.022831 | 0.06621 |  | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Penitentiary | 1.9 | 0.7 | 0.79 | 6 | 0.7 | 1 | 10% | 0.74761 | 0.5 | 2 | 0.54833 | 1 | 7 | 50 | 245 | 105 | 40 | 250 | 200 | 0.25 | 0.3 | 60 | 100 | 0.022831 | 0.06621 |  | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Performing Arts Theater | 1.8 | 2.6 | 1.14 | 4 | 2.6 | 1 | 10% | 0.74485 | 0.5 | 2 | 0.54833 | 1 | 7 | 75 | 245 | 105 | 14 | 225 | 105 | 0.76 | 0.2 | 60 | 100 | 0.022831 | 0.06621 |  | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Religious Building | 3.2 | 1.7 | 1.53 | 4 | 1.7 | 1 | 10% | 0.73324 | 0.96 | 2 | 0.54833 | 1 | 7 | 50 | 245 | 105 | 8 | 245 | 155 | 0.66 | 0.3 | 60 | 50 | 0.022831 | 0.06621 |  | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Sports Arena | 0.5 | 0.4 | 0.43 | 4 | 0.4 | 1 | 10% | 0.74485 | 1 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 0 | 245 | 105 | 0.3 | 0.3 | 120 | 100 | 0.022831 | 0.06621 |  | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Transportation Facility | 1 | 0.5 | 0.54 | 4 | 0.5 | 1 | 10% | 0.74761 | 0.5 | 2 | 0.54833 | 1 | 7 | 100 | 250 | 250 | 10 | 225 | 105 | 0.81 | 0.2 | 120 | 215 | 0.022831 | 0.06621 |  | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
CS Audience Seating Area, Other | 1.6 | 0.9 | 0.79 | 6 | 0.9 | 1 | 10% | 0.74761 | UWBD | 2 | 0.54833 | 1 | 7 | 50 | 245 | 105 | UWBD | UWBD | UWBD | UWBD | 0.3 | 60 | 100 | 0.022831 | 0.06621 |  | Use parent schedule | ps | Schedule is inherited
CS Atrium, Less than or equal to 40 ft | 1.3 | 0.6 | 0.03 (watts per ft height) | n.a. | 0.0375 per ft of height | 1 | 10% | n.a. | UWBD | n.a. | n.a. | n.a. | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.1 | 120 | 0 | 0.022831 | 0.06621 |  | Use parent schedule | ps | Schedule is inherited
CS Atrium, More than 40 ft | 0.2 | 0.2 | 0.02 (watts per ft height) | n.a. | 0.05 + 0.025 per ft of height | 1 | 10% | n.a. | UWBD | n.a. | n.a. | n.a. | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.1 | 120 | 0 | 0.022831 | 0.06621 |  | Use parent schedule | ps | Schedule is inherited
CS Banking Activity Area, | 2.4 | 1.5 | 1.38 | 6 | 1.5 | 1 | 10% | 1.7201 | 0.75 | 2 | 0.77138 | 1 | 7 | 200 | 250 | 250 | 200 | 250 | 200 | 0.09 | 0.1 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
CS Classroom/Lecture/Training, Penitentiary | 1.6 | 1.4 | 1.24 | 4 | 1.3 | 1 | n.a. | 0.58913 | 0.5 | 2 | 0.18587 | 1 | 7 | 75 | 245 | 155 | 40 | 250 | 200 | 0.25 | 0.2 | 120 | 215 | 0.13699 | 0.057078 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Classroom/Lecture/Training, K-12, laboratory and shops | 1.6 | 1.4 | 1.24 | 4 | 1.4 | 1 | 30% | 0.58913 | 1.39 | 2 | 0.18587 | 1 | 7 | 75 | 245 | 155 | 40 | 250 | 200 | 0.47 | 0.2 | 120 | 215 | 0.13699 | 0.057078 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Classroom/Lecture/Training, Other | 1.6 | 1.4 | 1.24 | 4 | 1.4 | 1 | n.a. | 0.58913 | UWBD | 2 | 0.18587 | 1 | 7 | 75 | 245 | 155 | UWBD | UWBD | UWBD | UWBD | 0.2 | 120 | 215 | 0.13699 | 0.057078 | Residential | Use parent schedule | ps | Schedule is inherited
CS Conference/Meeting/Multipurpose, | 1.5 | 1.3 | 1.23 | 6 | 1.3 | 1 | n.a. | 0.73324 | UWBD | 2 | 0.54833 | 1 | 7 | 50 | 245 | 155 | UWBD | UWBD | UWBD | UWBD | 0.4 | 60 | 150 | 0.2968 | 0.052511 |  | Use parent schedule | ps | Schedule is inherited
CS Confinment Cells, | 1.1 | 0.9 | 1.1 | 6 | 0.9 | 1 | 10% | 1.4928 | 0.5 | 2 | 1.1152 | 1 | 7 | 250 | 250 | 200 | 40 | 250 | 200 | 0.25 | 0.08 | 120 | 1110 | 0.69635 | 0.10274 |  | C-3 Hotel Motel | D | Hotel, motel, penitentiary
CS Copy/Print Room, | #N/A | 1.9 | 1.59 | 6 | 0.9 | 1 | 10% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | n.a. | n.a. | n.a. | UWBD | UWBD | UWBD | UWBD | n.a. | n.a. | n.a. | n.a. | n.a. | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Corridor, Assisted Living | #N/A | #N/A | 0.66 | Width<8 ft | 1.15 | 1 | 25% | 1.4046 | UWBD | 2 | 1.1152 | 1 | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.2 | 0 | 0 | 0.69635 | 0.10274 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Corridor, Hospital | 1.6 | 1 | 0.89 | Width < 8 ft | 1 | 1 | 25% | 1.2488 | UWBD | 2 | 0.76208 | 1 | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.2 | 0 | 0 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
CS Corridor, Manufacturing | 0.5 | 0.5 | 0.41 | Width < 8 ft | 0.5 | 1 | 25% | 0.34481 | 1 | 2 | 0.18587 | 1 | 7 | 1000 | 250 | 250 | 143 | 580 | 870 | 0.25 | 0.05 | 0 | 0 | 0.022831 | 0.06621 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
CS Corridor, Other | 0.7 | 0.5 | 0.66 | Width<8 ft | 0.5 | 1 | 25% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | 1000 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.05 | 0 | 0 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Courtroom, | 2.1 | 1.9 | 1.72 | 6 | 1.9 | 1 | 10% | 1.4928 | 0.25 | 2 | 1.1152 | 1 | 7 | 75 | 250 | 200 | 14 | 250 | 200 | 0.41 | 0.2 | 120 | 100 | 0.17123 | 0.046804 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
CS Computer Room, | 0.8 | 1.2 | 0.95 | 6 | 2.14 | 1 | 35% | n.a. | n. a. | n.a. | n.a. | n.a. | 7 | n.a. | 250 | 200 | n. a. | n. a. | n. a. | n. a. | n.a. | 120 | n.a. | n.a. | n.a. | Non-Residential | C-13 Data Center | X2 | Data center
CS Dining Area, Penitentiary | 1.8 | 1.4 | 0.9 | n.a. | 1.3 | 1 | 35% | 1.263 | 6 | 2 | 0.92937 | 1 | 7 | 100 | 275 | 275 | 10 | 275 | 275 | 0.93 | 0.2 | 385 | 400 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Assisted Living | 1.9 | 1.6 | 0.89 | n.a. | 3.32 | 1 | 35% | 1.3161 | 6 | 2 | 0.92937 | 1 | 7 | 100 | 275 | 275 | 10 | 275 | 275 | 0.93 | 0.3 | 385 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Bar Lounge/Leisure | 1.2 | 1.4 | 1.31 | 4 | 1.4 | 1 | 35% | 1.263 | 6 | 2 | 0.92937 | 1 | 7 | 100 | 275 | 275 | 10 | 275 | 275 | 0.93 | 0.3 | 120 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Cafeteria or Fast Food | 1.8 | 1.4 | 0.9 | n.a. | 0.9 | 1 | 35% | 1.3684 | 6 | 2 | 0.92937 | 1 | 7 | 100 | 275 | 275 | 10 | 275 | 275 | 0.93 | 0.2 | 385 | 400 | 17.5342 | 1.1267 | Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Family Dining | 2.2 | 2.1 | 0.89 | 4 | 2.1 | 1 | 35% | 1.3161 | 6 | 2 | 0.92937 | 1 | 7 | 100 | 250 | 250 | 14 | 275 | 275 | 0.71 | 0.2 | 0 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Other | 1.4 | 0.9 | 0.65 | 4 | 0.9 | 1 | 35% | 1.3161 | 6 | 2 | 0.92937 | 1 | 7 | 100 | 275 | 275 | 14 | 275 | 275 | 0.71 | 0.2 | 385 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Electrical/Mechanical , | 1.3 | 1.5 | 0.95 | 6 | 1.5 | 1 | 30% | UWBD | n. a. | UWBD | UWBD | UWBD | 7 | n.a. | 250 | 250 | n. a. | n. a. | n. a. | n. a. | n.a. | 0 | n.a. | n.a. | n.a. | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Emergency Vehicle Garage, | 1.3 | 1.5 | 0.95 | 6 | 0.8 | 1 | 10% | 0.57608 | UWBD | 2 | 0.54833 | 1 | 7 | 2000 | 250 | 200 | UWBD | UWBD | UWBD | UWBD | 0.05 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
CS Food Preparation , | 2.2 | 1.2 | 0.99 | 6 | 1.2 | 1 | 30% | 1.3161 | UWBD | 2 | 0.92937 | 1 | 7 | 200 | 275 | 475 | UWBD | UWBD | UWBD | UWBD | 0.3 | 385 | 400 | 35.0685 | 2.2534 | Residential | C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
CS Guest Room, | 2.5 | 1.1 | 1.11 | 6 | 1.1 | 1 | 45% | 1.5641 | 1.11 | 2 | 0.2974 | 1 | 7 | 250 | 245 | 155 | 250 | 250 | 200 | 0.08 | 0.12 | 2800 | 2000 | 0.69635 | 0.10274 | Non-Residential | C-3 Hotel Motel | D | Hotel, motel, penitentiary
CS Judges Chambers, | 1.1 | 1.3 | 1.17 | 8 | 1.3 | 1 | 30% | 1.4928 | 0.75 | 2 | 1.1152 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.09 | 0.1 | 120 | 300 | 0.17123 | 0.046804 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
CS Laboratory, Classrooms | 1.6 | 1.4 | 1.28 | 6 | 1.4 | 1 | None | 3.3415 | UWBD | 2 | 2.7881 | 1 | 7 | 75 | 245 | 155 | UWBD | UWBD | UWBD | UWBD | 0.2 | 120 | 215 | 0.2968 | 0.052511 | Non-Residential | C-9 Schools | G | K-12 schools, universities
CS Laboratory, Other | 1.8 | 1.4 | 1.81 | 6 | 1.4 | 1 | 10% | 3.3415 | n. a. | 2 | 2.7881 | 1 | 7 | 200 | 250 | 200 | n. a. | n. a. | n. a. | n. a. | 0.1 | 120 | 600 | n.a. | n.a. | Non-Residential | C-11 Laboratory | X1 | Laboratory
CS Laundry/Washing Area, | 0.7 | 0.6 | 0.6 | 4 | 0.6 | 1 | 10% | 0.51912 | n. a. | 2 | 0.54833 | 1 | 7 | 200 | 250 | 250 | n. a. | n. a. | n. a. | n. a. | 0.125 | 385 | 215 | n.a. | n.a. | Residential | Use parent schedule | ps | Schedule is inherited
CS Loading Dock, Interior, | 1.1 | 0.9 | 0.58 | 4 | 0.59 | 1 | 10% | n.a. | 0.24 | n.a. | n.a. | n.a. | 7 | 1000 | 275 | 475 | 0 | 275 | 475 | 0.06 | 0.05 | 120 | 225 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | L | Warehouse
CS Lobby, Assisted Living | 1.8 | 1.3 | 0.9 | 4 | 2.26 | 1 | 25% | 1.4046 | 1.11 | 2 | 1.1152 | 1 | 7 | 100 | 250 | 250 | 250 | 250 | 200 | 0.08 | 0.15 | 120 | 100 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | F | Dormatory, multifamily
CS Lobby, Elevator | 1.8 | 1.3 | 0.64 | 6 | 0.8 | 1 | 25% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.15 | 60 | 100 | 0.022831 | 0.06621 | Residential | Use parent schedule | ps | Schedule is inherited
CS Lobby, Hotel | 1.7 | 1.1 | 1.06 | 4 | 1.1 | 1 | 25% | 1.5641 | 1.11 | 2 | 0.2974 | 1 | 7 | 100 | 250 | 250 | 250 | 250 | 200 | 0.08 | 0.15 | 120 | 100 | 0.022831 | 0.06621 | Non-Residential | C-3 Hotel Motel | D | Hotel, motel, penitentiary
CS Lobby, Motion Picture Theater | 0.8 | 1.1 | 2 | 6 | 1.1 | 1 | 25% | 0.74485 | 0.54 | 2 | 0.54833 | 1 | 7 | 100 | 250 | 250 | 7 | 225 | 105 | 1.19 | 0.2 | 60 | 0 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Lobby, Performing Arts Theater | 1.2 | 3.3 | 0.52 | 4 | 3.3 | 1 | 25% | 0.74485 | 0.5 | 2 | 0.54833 | 1 | 7 | 100 | 250 | 250 | 14 | 225 | 105 | 0.76 | 0.2 | 60 | 0 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Lobby, Other | 1.8 | 1.3 | 0.9 | 4 | 1.3 | 1 | 25% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.15 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Locker Room , | 0.8 | 0.6 | 0.75 | 6 | 0.6 | 1 | 25% | n.a. | n. a. | n.a. | n.a. | n.a. | 7 | 100 | 250 | 200 | n. a. | n. a. | n. a. | n. a. | 0.5 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Lounge/Break, Healthcare | 1.4 | 0.8 | 1.07 | 6 | 0.8 | 1 | n.a. | 1.2488 | UWBD | 2 | 0.76208 | 1 | 7 | 100 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.2 | 120 | 0 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
CS Lounge/Break, Other | 1.4 | 1.2 | 0.73 | 4 | 1.2 | 1 | n.a. | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | 100 | 275 | 275 | UWBD | UWBD | UWBD | UWBD | 0.2 | 60 | 300 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Office, Enclosed | 1.5 | 1.1 | 1.11 | 8 | 1.1 | 1 | 30% | 1.6721 | 0.75 | 2 | 0.77138 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.09 | 0.1 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
CS Office, Open Plan | 1.3 | 1.1 | 0.98 | 4 | 1.1 | 1 | 15% | 1.6721 | 0.75 | 2 | 0.77138 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.09 | 0.1 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
CS Parking Area, Interior, | 0.2 | 0.2 | 0.19 | 4 | 0.2 | 1 | 15% | n.a. | 0 | n.a. | n.a. | n.a. | 7 | Uncond. | 250 | 200 | 0 | 250 | 200 | 0 | 0 | 120 | 0 | 0 | 0.031963 | Non-Residential | C-6 Parking Garage | K | Parking garage
CS Pharmacy Area, | 2.3 | 1.2 | 1.14 | 6 | 1.2 | 1 | 10% | 0.54928 | 0.3 | 2 | 0.34387 | 1 | 7 | 200 | 250 | 200 | 67 | 250 | 200 | 0.23 | 0.075 | 120 | 150 | 0.091324 | 0.11758 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
CS Restrooms , Assisted Living | 1 | 0.9 | 0.98 | 8 | 1.52 | 1 | 45% | 1.4046 | 1.11 | 2 | 1.1152 | 1 | 7 | 300 | 250 | 250 | 250 | 250 | 200 | 0.08 | 0.167 | 0 | 0 | 0.69635 | 0.10274 | Residential | C-12 Residential | F | Dormatory, multifamily
CS Restrooms , Other | 1 | 0.9 | 0.98 | 8 | 0.9 | 1 | 45% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | 300 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.167 | 0 | 0 | n.a. | n.a. | Residential | Use parent schedule | ps | Schedule is inherited
CS Sales Area, | 2.1 | 1.7 | 1.68 | 6 | 1.7 | 1 | 10% | 0.54928 | 0.3 | 2 | 0.34387 | 1 | 7 | 300 | 250 | 200 | 67 | 250 | 200 | 0.23 | 0.2 | 120 | 135 | 0.091324 | 0.11758 | Non-Residential | C-8 Retail | C | Library, museum, retail
CS Seating Area General, | 1.6 | 0.9 | 0.79 | 6 | 0.68 | 1 | 10% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | n.a. | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | n.a. | UWBD | n.a. | n.a. | n.a. | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Stairway, | 0.9 | 0.6 | 0.69 | 10 | 0.6 | 1 | 75% | UWBD | UWBD | UWBD | UWBD | UWBD | 7 | 1000 | 250 | 250 | UWBD | UWBD | UWBD | UWBD | 0.05 | 0 | 0 | n.a. | n.a. | Residential | Use parent schedule | ps | Schedule is inherited
CS Storage, Hospital | 3 | 1.4 | 1.27 | 6 | 0.9 | 1 | 45% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.15 | 160 | 0 | 1.1301 | 0.08105 | Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
CS Storage, >= 50 ft² | 0.3 | 0.3 | 0.63 | 6 | 0.8 | 1 | 45% | 0.31395 | 0.24 | 2 | 0.18587 | 1 | 7 | 500 | 275 | 475 | 0 | 275 | 475 | 0.06 | 0.04 | 120 | 0 | 0 | 0.031963 | Residential | Use parent schedule | ps | Schedule is inherited
CS Storage, < 50 ft² | 1.1 | 0.8 | 0.63 | 6 | 0.8 | 1 | 45% | 0.31395 | 0.24 | 2 | 0.18587 | 1 | 7 | 1000 | 275 | 475 | 0 | 275 | 475 | 0.06 | 0.04 | 120 | 0 | 0 | 0.031963 | Non-Residential | Use parent schedule | ps | Schedule is inherited
CS Vehicular Maintenance, | 1.4 | 0.7 | 0.67 | 4 | 0.7 | 1 | 10% | 0.50325 | 1 | 2 | 0.54833 | 1 | 7 | 200 | 275 | 475 | 143 | 375 | 625 | 0.25 | 1.5 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
CS Workshop, | 2.5 | 1.9 | 1.59 | 6 | 1.9 | 1 | 10% | 0.42834 | 1 | 2 | 0.54833 | 1 | 7 | 300 | 250 | 200 | 143 | 635 | 965 | 0.25 | 0.5 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
SS Assisted Living, Chapel | 2.2 | 1.3 | 1.05 | n.a. | 2.77 | 1 | 10% | 1.4046 | 1.11 | 2 | 1.1152 | 1 | 7 | 100 | 250 | 250 | 250 | 250 | 200 | 0.08 | 0.15 | 120 | 200 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | F | Dormatory, multifamily
SS Assisted Living, Recreation Room | 1.4 | 1.2 | 0.73 | 4 | 3.02 | 1 | 10% | 1.4046 | 1.11 | 2 | 1.1152 | 1 | 7 | 100 | 275 | 275 | 250 | 250 | 200 | 0.08 | 0.2 | 60 | 300 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | F | Dormatory, multifamily
SS Convention Center, Exhibit Space | 3.3 | 1.3 | 1.45 | 4 | 1.3 | 1 | 35% | 0.74761 | 0.25 | 2 | 0.54833 | 1 | 7 | 50 | 245 | 155 | 20 | 250 | 200 | 0.31 | 0.3 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Dormitory, Living Quarters | 1.9 | 1.1 | 0.38 | 8 | 1.11 | 1 | 10% | 1.9561 | 1.11 | 2 | 0.2974 | 1 | 7 | 250 | 250 | 250 | 250 | 250 | 200 | 0.08 | 0.06 | 120 | 1700 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | F | Dormatory, multifamily
SS Fire Station, Sleeping Quarters | 1.1 | 0.3 | 0.25 | 6 | 0.3 | 1 | 10% | 1.5404 | 1.5 | 2 | 1.1152 | 1 | 7 | 250 | 250 | 250 | 33 | 250 | 200 | 0.21 | 0.06 | 120 | 1700 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | F | Dormatory, multifamily
SS Gymnasium/Fitness Center, Exercise Area | 1.1 | 0.9 | 0.72 | 4 | 0.9 | 1 | 35% | 0.67425 | 0.5 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 100 | 710 | 1090 | 0.26 | 0.4 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Gymnasium/Fitness Center, Playing Area | 1.9 | 1.4 | 1.2 | 4 | 1.4 | 1 | 35% | 0.67425 | 0.5 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 100 | 710 | 1090 | 0.26 | 0.4 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Healthcare, Emergency Room | 2.8 | 2.7 | 2.26 | 6 | 2.7 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.15 | 160 | 1000 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Exam/Treatment | 1.6 | 1.5 | 1.66 | 8 | 1.5 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.075 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Supply Room | 3 | 1.4 | 1.27 | 6 | 1.4 | 1 | 45% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.15 | 160 | 0 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Nursery | 1 | 0.6 | 0.88 | 6 | 0.6 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.125 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Nurses’ Station | 1.8 | 1 | 0.87 | 6 | 1 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.075 | 160 | 150 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Operating Room | 7.6 | 2.2 | 1.89 | 6 | 2.2 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.15 | 160 | 1000 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Patient Room | 1.2 | 0.7 | 0.62 | 6 | 0.7 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.125 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Physical Therapy | 1.9 | 0.9 | 0.91 | 6 | 0.9 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.125 | 160 | 150 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Recovery Room | 2.6 | 0.8 | 1.15 | 6 | 0.8 | 1 | 10% | 1.2488 | 2 | 2 | 0.76208 | 1 | 7 | 200 | 250 | 200 | 200 | 250 | 200 | 0.47 | 0.075 | 160 | 600 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Library, Reading Area | 1.8 | 1.2 | 0.93 | 4 | 1.2 | 1 | 15% | 0.93723 | 1.5 | 2 | 0.54833 | 1 | 7 | 200 | 250 | 200 | 100 | 250 | 200 | 0.11 | 0.075 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | C | Library, museum, retail
SS Library, Stacks | 1.9 | 1.7 | 1.71 | 4 | 1.7 | 1 | 15% | 0.93723 | 1.5 | 2 | 0.54833 | 1 | 7 | 200 | 250 | 200 | 100 | 250 | 200 | 0.11 | 0.075 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | C | Library, museum, retail
SS Manufacturing Facility, Detailed Manufacturing | 6.2 | 2.1 | 1.29 | 4 | 2.1 | 1 | 10% | 0.34481 | 1 | 2 | 0.18587 | 1 | 7 | 300 | 250 | 200 | 143 | 580 | 870 | 0.25 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, Equipment Room | 0.8 | 1.2 | 0.95 | 6 | 1.2 | 1 | 10% | 0.34481 | 1 | 2 | 0.18587 | 1 | 7 | 17500 | 375 | 625 | 143 | 580 | 870 | 0.25 | 0.05 | 120 | 1000 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, Extra High Bay (>50 ft Floor to Ceiling Height) | 3 | 1.7 | 1.05 | 4 | 1.32 | 1 | 10% | 0.34481 | 1 | 2 | 0.18587 | 1 | 7 | 300 | 375 | 625 | 143 | 580 | 870 | 0.25 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, High Bay (25–50 ft Floor to Ceiling Height) | 3 | 1.7 | 1.23 | 4 | 1.7 | 1 | 10% | 0.34481 | 1 | 2 | 0.18587 | 1 | 7 | 300 | 375 | 625 | 143 | 580 | 870 | 0.25 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, Low Bay (<25 ft Floor to Ceiling Height) | 2.1 | 1.2 | 1.19 | 4 | 1.2 | 1 | 10% | 0.34481 | 1 | 2 | 0.18587 | 1 | 7 | 300 | 375 | 625 | 143 | 580 | 870 | 0.25 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
SS Museum, General Exhibition | 1.6 | 1 | 1.05 | 6 | 1 | 1 | 10% | 0.74485 | 1.5 | 2 | 0.54833 | 1 | 7 | 50 | 250 | 250 | 25 | 250 | 200 | 0.36 | 0.3 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | C | Library, museum, retail
SS Museum, Restoration | 2.5 | 1.7 | 1.02 | 6 | 1.7 | 1 | 10% | 0.42834 | 1.5 | 2 | 0.54833 | 1 | 7 | 200 | 275 | 475 | 25 | 250 | 200 | 0.36 | 0.1 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-8 Retail | C | Library, museum, retail
SS Post Office, Sorting Area | 1.7 | 1.2 | 0.94 | 4 | 1.2 | 1 | 10% | 1.669 | 1 | 2 | 0.77138 | 1 | 7 | 300 | 250 | 206 | 33 | 250 | 200 | 0.21 | 0.25 | 106 | 175 | 0.022831 | 0.06621 | Non-Residential | C-5 Office | A | courthouse, office, post office, town hall
SS Religious Building, Fellowship Hall | 2.3 | 0.9 | 0.64 | 4 | 0.9 | 1 | 10% | 0.29845 | 0.96 | 2 | 0.54833 | 0.4 | 7 | 50 | 245 | 105 | 8 | 245 | 155 | 0.66 | 0.3 | 60 | 50 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Religious Building, Worship/Pulpit/Choir | 5.2 | 2.4 | 1.53 | 4 | 2.4 | 1 | 10% | 0.29845 | 0.96 | 2 | 0.54833 | 0.4 | 7 | 50 | 245 | 105 | 8 | 245 | 155 | 0.66 | 0.3 | 60 | 50 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Retail, Dressing/Fitting Room | 0.8 | 0.6 | 0.4 | 6 | 0.89 | 1 | 10% | 0.82157 | 0.3 | 2 | 0.34387 | 1 | 7 | 100 | 250 | 200 | 67 | 250 | 200 | 0.23 | 0.5 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | C-8 Retail | C | Library, museum, retail
SS Retail, Mall Concourse | 1.8 | 1.7 | 1.1 | 4 | 1.7 | 1 | 10% | 0 | 0.3 | 2 | 0.54833 | 1 | 7 | 200 | 250 | 250 | 67 | 250 | 200 | 0.23 | 0.1 | 120 | 215 | 0.091324 | 0.11758 | Retail | C-8 Retail | C | Library, museum, retail
SS Sports Arena Playing Area, Class I | 4.3 | 2.3 | 0.72 | 4 | 4.61 | 1 | 10% | 0.67425 | 1 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 0 | 245 | 105 | 0.3 | 0.4 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Sports Arena Playing Area, Class II | 4.3 | 2.3 | 1.2 | 4 | 3.01 | 1 | 10% | 0.67425 | 1 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 0 | 245 | 105 | 0.3 | 0.4 | 120 | 200 | 0.022831 | 0.06621 | Retail | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Sports Arena Playing Area, Class III | 4.3 | 2.3 | 1.92 | 4 | 2.26 | 1 | 10% | 0.67425 | 1 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 0 | 245 | 105 | 0.3 | 0.4 | 120 | 200 | 0.022831 | 0.06621 | Retail | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Sports Arena Playing Area, Class IV | 4.3 | 2.3 | 3.01 | 4 | 1.5 | 1 | 10% | 0.67425 | 1 | 2 | 0.54833 | 1 | 7 | 50 | 255 | 875 | 0 | 245 | 105 | 0.3 | 0.4 | 120 | 200 | 0.022831 | 0.06621 | Retail | C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Transportation, Baggage/Carousel Area | 1.3 | 1 | 0.76 | 4 | 1 | 1 | 10% | 0.76225 | 0.5 | 2 | 0.54833 | 1 | 7 | 200 | 250 | 250 | 10 | 225 | 105 | 0.81 | 0.1 | 120 | 215 | 0.022831 | 0.06621 | Retail | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Transportation, Concourse | 0.7 | 0.6 | 0.36 | 4 | 0.6 | 1 | 10% | 0.76225 | 0.5 | 2 | 0.54833 | 1 | 7 | 200 | 250 | 250 | 10 | 225 | 105 | 0.81 | 0.1 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Transportation, Ticket Counter | 1.8 | 1.5 | 1.08 | 4 | 1.5 | 1 | 10% | 0.76225 | 0.5 | 2 | 0.54833 | 1 | 7 | 100 | 250 | 250 | 10 | 225 | 105 | 0.81 | 0.2 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | E | Fire station, clinic, hospital, police station, transportation
SS Warehouse, Medium/Bulky Items on Pallets | 1.1 | 0.9 | 0.58 | 4 | 0.9 | 1 | 15% | 0.31395 | 0.24 | 2 | 0.18587 | 1 | 7 | 1000 | 275 | 475 | 0 | 275 | 475 | 0.06 | 0.05 | 120 | 225 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | L | Warehouse
SS Warehouse, Smaller Hand Carried Items | 1.6 | 1.4 | 0.95 | 6 | 1.4 | 1 | 15% | 0.31395 | 0.24 | 2 | 0.18587 | 1 | 7 | 500 | 275 | 475 | 0 | 275 | 475 | 0.06 | 0.05 | 120 | 225 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | L | Warehouse
UWBD = Use whole buildling data
Note on Y2: Source: CEUS
Note on Z2: Source: CEUS
Note on B3: Source: 90.1-2001
Note on C3: Source: 90.1-2007
Note on D3: Source: 90.1-2010
Note on E3: Source: 90.1-2010
Note on F3: Source: 90.1-2013BM
Note on G3: Source: ACM05
Note on H3: Charles Eley: This is only relevant for 90.1-2013-BM
Note on I3: Source: NREL 956 and Eley Analysis. See separate spreadsheet and documentation.
Note on K3: Source: NREL/TP-550-41956
Note on L3: Source: NREL/TP-550-41956
Note on M3: Source: NREL/TP-550-41956
Note on N3: Source: ACM05
Note on O3: Source: ECB-CS
Note on P3: Source: ACM05
Note on Q3: Source: ACM05
Note on R3: Charles Eley: Source SSPC 90.1 Envelope Trade-off Rules
Note on S3: Charles Eley: Source SSPC 90.1 Envelope Trade-off Rules
Note on T3: Charles Eley: Source SSPC 90.1 Envelope Trade-off Rules
Note on U3: Charles Eley: Source SSPC 90.1 Envelope Trade-off Rules
Note on V3: Source: ACM05
Note on W3: Source: ECB-CS
Note on X3: Source: ECB-CS
Note on AD3: Charles Eley: What do these refer to?
Note on A4: Charles Eley: These categories are consistent with Table G3.1.1-2
Note on A38: Charles Eley: These classifications are consistent with Table G3.7.

## bEQ Data
| 0 | Automatic Lighting Controls | Plug Loads | Occupancy | Occupancy | 0 | 0 | Ventilation Rate | 0 | Water Heating | Process | 0 | Schedules | Schedules | 0
| 0 | 0 |  | Heat Gain per Occupant (Btu/occ) | Occupant Heat Gain | 0 | 0 | 0 | California ACM 2005 |  | Interior Gas Appliance Power Density (Btu/h-ft²) | Refrigeration Power Density (W/ft²) | 0
| California 2005 ACM | Occupant Sensor Power Adjustment Factors | Default Power Density (W/ft²) | California 2005 ACM | Default Occupant Density (ft²/person) | Sensible Heat Gain (Btu/h-person) | Latent Heat Gain (Btu/h-person) | Ventilation Rate (Revised) (cfm/ft²) | Load (Btu/h-occ) | Load (Btu/h-occ) | 0 | 0 | California 2005 Schedule | Schedule from Appendix C | 0 | Description
Whole Building Categories | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BA Automotive Facility | 1 | n.a. | 0.50325 | 100 | 143 | 375 | 625 | 0.25 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
BA Convention Center | 0.96 | n.a. | 0.74761 | 7.3529 | 20 | 250 | 200 | 0.31 | 57 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Courthouse | 0.96 | n.a. | 1.669 | 7.3529 | 14 | 250 | 200 | 0.41 | 57 | 135 | 0.17123 | 0.046804 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
BA Dining: Bar Lounge/Leisure | 0.79 | n.a. | 1.3161 | 22.2222 | 10 | 275 | 275 | 0.93 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
BA Dining: Cafeteria/Fast Food | 0.79 | n.a. | 1.3684 | 22.2222 | 10 | 275 | 275 | 0.93 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
BA Dining: Family | 0.79 | n.a. | 1.263 | 22.2222 | 14 | 275 | 275 | 0.71 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
BA Dormitory | 0.5 | n.a. | 1.9561 | 200 | 100 | 250 | 200 | 0.11 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | C-12 Residential | 0 | Dormatory, multifamily
BA Exercise Center | 1 | n.a. | 0.67425 | 100 | 100 | 710 | 1090 | 0.26 | 120 | 135 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Fire Station | 1.5 | n.a. | 1.5404 | 100 | 33 | 250 | 200 | 0.21 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
BA Gymnasium | 0.5 | n.a. | 0.67425 | 50 | 33 | 710 | 1090 | 0.3 | 120 | 135 | 0.022831 | 0.06621 | Non-Residential | C-14 Gymnasium | 0 | Gymnasium
BA Healthcare Clinic | 1.18 | n.a. | 1.2202 | 100 | 200 | 250 | 200 | 0.47 | 110 | 135 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
BA Hospital | 1.18 | n.a. | 1.2488 | 100 | 200 | 250 | 200 | 0.47 | 110 | 135 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
BA Hotel | 0.5 | n.a. | 1.5641 | 200 | 250 | 250 | 200 | 0.08 | 2800 | 1700 | 0.69635 | 0.10274 | Hotel Function | C-3 Hotel Motel | 0 | Hotel, motel, penitentiary
BA Library | 1.5 | n.a. | 0.93723 | 100 | 100 | 250 | 200 | 0.11 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
BA Manufacturing Facility | 1 | n.a. | 0.34481 | 142.8571 | 143 | 580 | 870 | 0.25 | 120 | 225 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
BA Motel | 0.5 | n.a. | 1.5641 | 200 | 250 | 250 | 200 | 0.08 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | C-3 Hotel Motel | 0 | Hotel, motel, penitentiary
BA Motion Picture Theater | 1 | n.a. | 0.74485 | 6.993 | 7 | 225 | 105 | 1.19 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Multifamily | 0.5 | n.a. | 1.4245 | 200 | 380 | 250 | 200 | 0.06 | 1700 | 1700 | 0.69635 | 0.10274 | Residential | C-12 Residential | 0 | Dormatory, multifamily
BA Museum | 1.5 | n.a. | 0.74485 | 14.9254 | 25 | 250 | 200 | 0.36 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
BA Office | 1.34 | n.a. | 1.6721 | 100 | 200 | 250 | 200 | 0.09 | 106 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
BA Parking Garage | 1 | n.a. | n.a. | 100 | 0 | 250 | 200 | 0 | 120 | 0 | 0 | 0.031963 | Retail | C-6 Parking Garage | 0 | Parking garage
BA Penitentiary | 0.5 | n.a. | 1.4928 | 200 | 40 | 250 | 200 | 0.25 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | C-3 Hotel Motel | 0 | Hotel, motel, penitentiary
BA Performing Arts Theater | 0.5 | n.a. | 0.74485 | 6.993 | 14 | 225 | 105 | 0.76 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Police Station | 1.5 | n.a. | 1.5404 | 100 | 33 | 250 | 200 | 0.21 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
BA Post Office | 1 | n.a. | 0.90907 | 100 | 33 | 250 | 200 | 0.21 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
BA Religious Building | 0.96 | n.a. | 0.29845 | 7.3529 | 8 | 245 | 155 | 0.66 | 57 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Retail | 1 | n.a. | 0.70235 | 30.303 | 67 | 250 | 200 | 0.23 | 120 | 135 | 0.091324 | 0.11758 | Retail | C-8 Retail | 0 | Library, museum, retail
BA School/University | 1 | n.a. | 0.68748 | 25 | 40 | 250 | 200 | 0.47 | 108 | 215 | 0.13699 | 0.057078 | Non-Residential | C-9 Schools | 0 | K-12 schools, universities
BA Sports Arena | 1 | n.a. | 0.74761 | 6.993 | 0 | 245 | 105 | 0.3 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
BA Town Hall | 1.34 | n.a. | 0.74761 | 100 | 200 | 250 | 200 | 0.09 | 106 | 215 | 0.12557 | 0.053653 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
BA Transportation | 0.5 | n.a. | 0.51912 | 30.303 | 10 | 225 | 105 | 0.81 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
BA Warehouse | 0.2 | n.a. | 0.30231 | 333.3333 | 0 | 275 | 475 | 0.06 | 120 | 1000 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | 0 | Warehouse
BA Workshop | 1 | n.a. | 0.42834 | 142.8571 | 143 | 635 | 965 | 0.25 | 120 | 225 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
Space-by-Space Classifications | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CS Audience Seating Area, Auditorium | 1 | 10% | 0.74761 | 7 | 14 | 225 | 105 | 0.76 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Audience Seating Area, Convention Center | 1 | 10% | 0.74761 | 7 | 20 | 250 | 200 | 0.31 | 60 | 150 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Exercise Center | 1 | 10% | 0.67425 | 7 | 100 | 710 | 1090 | 0.26 | 120 | 100 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Audience Seating Area, Gymnasium | 1 | 10% | 0.67425 | 7 | 33 | 710 | 1090 | 0.3 | 120 | 100 | 0.022831 | 0.06621 | 0 | Use parent schedule | 0 | Schedule is inherited
CS Audience Seating Area, Motion Picture Theater | 1 | 10% | 0.74485 | 7 | 7 | 225 | 105 | 1.19 | 60 | 100 | 0.022831 | 0.06621 | 0 | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Penitentiary | 1 | 10% | 0.74761 | 7 | 40 | 250 | 200 | 0.25 | 60 | 100 | 0.022831 | 0.06621 | 0 | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Performing Arts Theater | 1 | 10% | 0.74485 | 7 | 14 | 225 | 105 | 0.76 | 60 | 100 | 0.022831 | 0.06621 | 0 | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Religious Building | 1 | 10% | 0.73324 | 7 | 8 | 245 | 155 | 0.66 | 60 | 50 | 0.022831 | 0.06621 | 0 | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Sports Arena | 1 | 10% | 0.74485 | 7 | 0 | 245 | 105 | 0.3 | 120 | 100 | 0.022831 | 0.06621 | 0 | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Audience Seating Area, Transportation Facility | 1 | 10% | 0.74761 | 7 | 10 | 225 | 105 | 0.81 | 120 | 215 | 0.022831 | 0.06621 | 0 | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
CS Audience Seating Area, Other | 1 | 10% | 0.74761 | 7 | UWBD | UWBD | UWBD | UWBD | 60 | 100 | 0.022831 | 0.06621 | 0 | Use parent schedule | 0 | Schedule is inherited
CS Atrium, Less than or equal to 40 ft | 1 | 10% | n.a. | 7 | UWBD | UWBD | UWBD | UWBD | 120 | 0 | 0.022831 | 0.06621 | 0 | Use parent schedule | 0 | Schedule is inherited
CS Atrium, More than 40 ft | 1 | 10% | n.a. | 7 | UWBD | UWBD | UWBD | UWBD | 120 | 0 | 0.022831 | 0.06621 | 0 | Use parent schedule | 0 | Schedule is inherited
CS Banking Activity Area, | 1 | 10% | 1.7201 | 7 | 200 | 250 | 200 | 0.09 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
CS Classroom/Lecture/Training, Penitentiary | 1 | n.a. | 0.58913 | 7 | 40 | 250 | 200 | 0.25 | 120 | 215 | 0.13699 | 0.057078 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Classroom/Lecture/Training, K-12, laboratory and shops | 1 | 30% | 0.58913 | 7 | 40 | 250 | 200 | 0.47 | 120 | 215 | 0.13699 | 0.057078 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Classroom/Lecture/Training, Other | 1 | n.a. | 0.58913 | 7 | UWBD | UWBD | UWBD | UWBD | 120 | 215 | 0.13699 | 0.057078 | Residential | Use parent schedule | 0 | Schedule is inherited
CS Conference/Meeting/Multipurpose, | 1 | n.a. | 0.73324 | 7 | UWBD | UWBD | UWBD | UWBD | 60 | 150 | 0.2968 | 0.052511 | 0 | Use parent schedule | 0 | Schedule is inherited
CS Confinment Cells, | 1 | 10% | 1.4928 | 7 | 40 | 250 | 200 | 0.25 | 120 | 1110 | 0.69635 | 0.10274 | 0 | C-3 Hotel Motel | 0 | Hotel, motel, penitentiary
CS Copy/Print Room, | 1 | 10% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | n.a. | n.a. | n.a. | n.a. | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Corridor, Assisted Living | 1 | 25% | 1.4046 | 7 | UWBD | UWBD | UWBD | UWBD | 0 | 0 | 0.69635 | 0.10274 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Corridor, Hospital | 1 | 25% | 1.2488 | 7 | UWBD | UWBD | UWBD | UWBD | 0 | 0 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
CS Corridor, Manufacturing | 1 | 25% | 0.34481 | 7 | 143 | 580 | 870 | 0.25 | 0 | 0 | 0.022831 | 0.06621 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
CS Corridor, Other | 1 | 25% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | 0 | 0 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Courtroom, | 1 | 10% | 1.4928 | 7 | 14 | 250 | 200 | 0.41 | 120 | 100 | 0.17123 | 0.046804 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
CS Computer Room, | 1 | 35% | n.a. | 7 | n. a. | n. a. | n. a. | n. a. | 120 | n.a. | n.a. | n.a. | Non-Residential | C-13 Data Center | 0 | Data center
CS Dining Area, Penitentiary | 1 | 35% | 1.263 | 7 | 10 | 275 | 275 | 0.93 | 385 | 400 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Assisted Living | 1 | 35% | 1.3161 | 7 | 10 | 275 | 275 | 0.93 | 385 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Bar Lounge/Leisure | 1 | 35% | 1.263 | 7 | 10 | 275 | 275 | 0.93 | 120 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Cafeteria or Fast Food | 1 | 35% | 1.3684 | 7 | 10 | 275 | 275 | 0.93 | 385 | 400 | 17.5342 | 1.1267 | Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Family Dining | 1 | 35% | 1.3161 | 7 | 14 | 275 | 275 | 0.71 | 0 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Dining Area, Other | 1 | 35% | 1.3161 | 7 | 14 | 275 | 275 | 0.71 | 385 | 300 | 17.5342 | 1.1267 | Non-Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Electrical/Mechanical , | 1 | 30% | UWBD | 7 | n. a. | n. a. | n. a. | n. a. | 0 | n.a. | n.a. | n.a. | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Emergency Vehicle Garage, | 1 | 10% | 0.57608 | 7 | UWBD | UWBD | UWBD | UWBD | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
CS Food Preparation , | 1 | 30% | 1.3161 | 7 | UWBD | UWBD | UWBD | UWBD | 385 | 400 | 35.0685 | 2.2534 | Residential | C-7 Restaurant | 0 | Cafeteria, fast food, family dining, bar, lounge
CS Guest Room, | 1 | 45% | 1.5641 | 7 | 250 | 250 | 200 | 0.08 | 2800 | 2000 | 0.69635 | 0.10274 | Non-Residential | C-3 Hotel Motel | 0 | Hotel, motel, penitentiary
CS Judges Chambers, | 1 | 30% | 1.4928 | 7 | 200 | 250 | 200 | 0.09 | 120 | 300 | 0.17123 | 0.046804 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
CS Laboratory, Classrooms | 1 | None | 3.3415 | 7 | UWBD | UWBD | UWBD | UWBD | 120 | 215 | 0.2968 | 0.052511 | Non-Residential | C-9 Schools | 0 | K-12 schools, universities
CS Laboratory, Other | 1 | 10% | 3.3415 | 7 | n. a. | n. a. | n. a. | n. a. | 120 | 600 | n.a. | n.a. | Non-Residential | C-11 Laboratory | 0 | Laboratory
CS Laundry/Washing Area, | 1 | 10% | 0.51912 | 7 | n. a. | n. a. | n. a. | n. a. | 385 | 215 | n.a. | n.a. | Residential | Use parent schedule | 0 | Schedule is inherited
CS Loading Dock, Interior, | 1 | 10% | n.a. | 7 | 0 | 275 | 475 | 0.06 | 120 | 225 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | 0 | Warehouse
CS Lobby, Assisted Living | 1 | 25% | 1.4046 | 7 | 250 | 250 | 200 | 0.08 | 120 | 100 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | 0 | Dormatory, multifamily
CS Lobby, Elevator | 1 | 25% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | 60 | 100 | 0.022831 | 0.06621 | Residential | Use parent schedule | 0 | Schedule is inherited
CS Lobby, Hotel | 1 | 25% | 1.5641 | 7 | 250 | 250 | 200 | 0.08 | 120 | 100 | 0.022831 | 0.06621 | Non-Residential | C-3 Hotel Motel | 0 | Hotel, motel, penitentiary
CS Lobby, Motion Picture Theater | 1 | 25% | 0.74485 | 7 | 7 | 225 | 105 | 1.19 | 60 | 0 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Lobby, Performing Arts Theater | 1 | 25% | 0.74485 | 7 | 14 | 225 | 105 | 0.76 | 60 | 0 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
CS Lobby, Other | 1 | 25% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Locker Room , | 1 | 25% | n.a. | 7 | n. a. | n. a. | n. a. | n. a. | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Lounge/Break, Healthcare | 1 | n.a. | 1.2488 | 7 | UWBD | UWBD | UWBD | UWBD | 120 | 0 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
CS Lounge/Break, Other | 1 | n.a. | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | 60 | 300 | 0.022831 | 0.06621 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Office, Enclosed | 1 | 30% | 1.6721 | 7 | 200 | 250 | 200 | 0.09 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
CS Office, Open Plan | 1 | 15% | 1.6721 | 7 | 200 | 250 | 200 | 0.09 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
CS Parking Area, Interior, | 1 | 15% | n.a. | 7 | 0 | 250 | 200 | 0 | 120 | 0 | 0 | 0.031963 | Non-Residential | C-6 Parking Garage | 0 | Parking garage
CS Pharmacy Area, | 1 | 10% | 0.54928 | 7 | 67 | 250 | 200 | 0.23 | 120 | 150 | 0.091324 | 0.11758 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
CS Restrooms , Assisted Living | 1 | 45% | 1.4046 | 7 | 250 | 250 | 200 | 0.08 | 0 | 0 | 0.69635 | 0.10274 | Residential | C-12 Residential | 0 | Dormatory, multifamily
CS Restrooms , Other | 1 | 45% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | 0 | 0 | n.a. | n.a. | Residential | Use parent schedule | 0 | Schedule is inherited
CS Sales Area, | 1 | 10% | 0.54928 | 7 | 67 | 250 | 200 | 0.23 | 120 | 135 | 0.091324 | 0.11758 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
CS Seating Area General, | 1 | 10% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | UWBD | n.a. | n.a. | n.a. | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Stairway, | 1 | 75% | UWBD | 7 | UWBD | UWBD | UWBD | UWBD | 0 | 0 | n.a. | n.a. | Residential | Use parent schedule | 0 | Schedule is inherited
CS Storage, Hospital | 1 | 45% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 0 | 1.1301 | 0.08105 | Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
CS Storage, >= 50 ft² | 1 | 45% | 0.31395 | 7 | 0 | 275 | 475 | 0.06 | 120 | 0 | 0 | 0.031963 | Residential | Use parent schedule | 0 | Schedule is inherited
CS Storage, < 50 ft² | 1 | 45% | 0.31395 | 7 | 0 | 275 | 475 | 0.06 | 120 | 0 | 0 | 0.031963 | Non-Residential | Use parent schedule | 0 | Schedule is inherited
CS Vehicular Maintenance, | 1 | 10% | 0.50325 | 7 | 143 | 375 | 625 | 0.25 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
CS Workshop, | 1 | 10% | 0.42834 | 7 | 143 | 635 | 965 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
SS Assisted Living, Chapel | 1 | 10% | 1.4046 | 7 | 250 | 250 | 200 | 0.08 | 120 | 200 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | 0 | Dormatory, multifamily
SS Assisted Living, Recreation Room | 1 | 10% | 1.4046 | 7 | 250 | 250 | 200 | 0.08 | 60 | 300 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | 0 | Dormatory, multifamily
SS Convention Center, Exhibit Space | 1 | 35% | 0.74761 | 7 | 20 | 250 | 200 | 0.31 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Dormitory, Living Quarters | 1 | 10% | 1.9561 | 7 | 250 | 250 | 200 | 0.08 | 120 | 1700 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | 0 | Dormatory, multifamily
SS Fire Station, Sleeping Quarters | 1 | 10% | 1.5404 | 7 | 33 | 250 | 200 | 0.21 | 120 | 1700 | 0.69635 | 0.10274 | Non-Residential | C-12 Residential | 0 | Dormatory, multifamily
SS Gymnasium/Fitness Center, Exercise Area | 1 | 35% | 0.67425 | 7 | 100 | 710 | 1090 | 0.26 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Gymnasium/Fitness Center, Playing Area | 1 | 35% | 0.67425 | 7 | 100 | 710 | 1090 | 0.26 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Healthcare, Emergency Room | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 1000 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Exam/Treatment | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Supply Room | 1 | 45% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 0 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Nursery | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Nurses’ Station | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 150 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Operating Room | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 1000 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Patient Room | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Physical Therapy | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 150 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Healthcare, Recovery Room | 1 | 10% | 1.2488 | 7 | 200 | 250 | 200 | 0.47 | 160 | 600 | 1.1301 | 0.08105 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Library, Reading Area | 1 | 15% | 0.93723 | 7 | 100 | 250 | 200 | 0.11 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
SS Library, Stacks | 1 | 15% | 0.93723 | 7 | 100 | 250 | 200 | 0.11 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
SS Manufacturing Facility, Detailed Manufacturing | 1 | 10% | 0.34481 | 7 | 143 | 580 | 870 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, Equipment Room | 1 | 10% | 0.34481 | 7 | 143 | 580 | 870 | 0.25 | 120 | 1000 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, Extra High Bay (>50 ft Floor to Ceiling Height) | 1 | 10% | 0.34481 | 7 | 143 | 580 | 870 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, High Bay (25–50 ft Floor to Ceiling Height) | 1 | 10% | 0.34481 | 7 | 143 | 580 | 870 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
SS Manufacturing Facility, Low Bay (<25 ft Floor to Ceiling Height) | 1 | 10% | 0.34481 | 7 | 143 | 580 | 870 | 0.25 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-4 Manufacturing | 0 | Automotive facility, workshop, manufacturing facility
SS Museum, General Exhibition | 1 | 10% | 0.74485 | 7 | 25 | 250 | 200 | 0.36 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
SS Museum, Restoration | 1 | 10% | 0.42834 | 7 | 25 | 250 | 200 | 0.36 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
SS Post Office, Sorting Area | 1 | 10% | 1.669 | 7 | 33 | 250 | 200 | 0.21 | 106 | 175 | 0.022831 | 0.06621 | Non-Residential | C-5 Office | 0 | courthouse, office, post office, town hall
SS Religious Building, Fellowship Hall | 1 | 10% | 0.29845 | 7 | 8 | 245 | 155 | 0.66 | 60 | 50 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Religious Building, Worship/Pulpit/Choir | 1 | 10% | 0.29845 | 7 | 8 | 245 | 155 | 0.66 | 60 | 50 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Retail, Dressing/Fitting Room | 1 | 10% | 0.82157 | 7 | 67 | 250 | 200 | 0.23 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | C-8 Retail | 0 | Library, museum, retail
SS Retail, Mall Concourse | 1 | 10% | 0 | 7 | 67 | 250 | 200 | 0.23 | 120 | 215 | 0.091324 | 0.11758 | Retail | C-8 Retail | 0 | Library, museum, retail
SS Sports Arena Playing Area, Class I | 1 | 10% | 0.67425 | 7 | 0 | 245 | 105 | 0.3 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Sports Arena Playing Area, Class II | 1 | 10% | 0.67425 | 7 | 0 | 245 | 105 | 0.3 | 120 | 200 | 0.022831 | 0.06621 | Retail | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Sports Arena Playing Area, Class III | 1 | 10% | 0.67425 | 7 | 0 | 245 | 105 | 0.3 | 120 | 200 | 0.022831 | 0.06621 | Retail | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Sports Arena Playing Area, Class IV | 1 | 10% | 0.67425 | 7 | 0 | 245 | 105 | 0.3 | 120 | 200 | 0.022831 | 0.06621 | Retail | C-1 Assembly | 0 | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
SS Transportation, Baggage/Carousel Area | 1 | 10% | 0.76225 | 7 | 10 | 225 | 105 | 0.81 | 120 | 215 | 0.022831 | 0.06621 | Retail | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Transportation, Concourse | 1 | 10% | 0.76225 | 7 | 10 | 225 | 105 | 0.81 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Transportation, Ticket Counter | 1 | 10% | 0.76225 | 7 | 10 | 225 | 105 | 0.81 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | C-2 Public | 0 | Fire station, clinic, hospital, police station, transportation
SS Warehouse, Medium/Bulky Items on Pallets | 1 | 15% | 0.31395 | 7 | 0 | 275 | 475 | 0.06 | 120 | 225 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | 0 | Warehouse
SS Warehouse, Smaller Hand Carried Items | 1 | 15% | 0.31395 | 7 | 0 | 275 | 475 | 0.06 | 120 | 225 | 0 | 0.031963 | Non-Residential | C-10 Warehouse | 0 | Warehouse
UWBD = Use whole building data

## Notes
Rev 9 Release Notes
2016-07-24
1 | This revision adds data from the SSPC 90.1 website that is intended for use with the building envelope tradeoff
procedure (the successor to EnvStd). This data includes references to a set of schedules labeled A through K, and
also includes data on plug loads, ventilation rates, occupant density and heat gain (sensible and latent).
2 | The first column labels are modified to be consistent with the lighting power Table G3.7 of 90.1-2016. Previously the
data from 90.1-2010 was used.
3 | Control credits updated for the 90.1-2016 version.
4 | References to schedules was updated in response to changes to appendix C.
5 | The assumption is made that both a building type and a space type are selected. In some instances, the
information for the building type becomes the value for the space type.
6 | Updated mappings.
7 | Added an option for "use parent data" to the lists for appropriate space-by-space data. In the schedules column
"Use parent schedule" is the key. For other data "UWBD" (use whole building data) is the key. For some
space-by-space categories no default is offered, e.g. data centers.
Use
Parent
| Code | Source of data | Relevance | No default | Option | Notes
| 90.1-2016 BM | ASHRAE Standard 90.1-2016 PRM (BM) | BM baseline |  |  | This is the pick list
| 90.1-2001 | ASHRAE Standard 90.1-2001 | Baseline for IRS 179D |  |  | Baseline for IRS 179d (expired)
| 90.1-2007 | ASHRAE Standard 90.1-2007 | Baseline for LEED 2.2
| 90.1-2010 | ASHRAE Standard 90.1-2010 | Baseline for LEED 2012
| SSPC 90.1 | Addendum "an" Schedules and Loads | Plugs, ventilation, occupants and schedules | P | P | Used for
| CBECS-2003 | Methodology for Modeling . ., NREL 550-41956 | Data for plug loads and other assumptions | P | P
| CEUS | California Energy Utilization Survey, Iron, 2006 | Data source for refrigeration and cooking power | P | P
| ECB-CS | Unpublished ECB Compliance Supplement | Data source | P | P
| ACM05 | California 2005 ACM Manual | Referenced by IRS 179D | P | P | No longer relevant
Rev 8 Release Notes
2015-08-27
1 | This revision adds the lighting power numbers from the 90.1-2013 PRM with the BM and DX addenda. It also hides
the ACM 2005 modeling assumptions since the tax credit has expired and these data were only used for that
purpose. Lighting power density values for 90.1-2013-BM are taken from a document prepared by Eley and
Rosenberg titled "Appendix G 2013+BM and DX.docx".
2 | The lighting control credits in Table 9.6.2 of 90.1-2013-BM are added to the table.
3 | The equipment power density values have been modified based on changes to the underlying spreadsheet,
"COMNET Plug Load Calcs (Rev3).xlsx'. See this spreadsheet for additional information.
4 | Control credits added for the 90.1-2016 BM purpose. These were based on a preliminary release of the standard
Rev 7 Release Notes
2014-06-26
This revision makes the mapping between the pick lists (whole building and space-by-space) and the data sources
more explicit. Gas and electric process energy is also treated differently; it is explicitely mapped to the original
source of the data (CEUS). The spreadsheet is structured so that a change on the "Mapping" tab triggers the
updates on the "Modeling Data" tab. The stipple pattern indicates that the value changed from the previous version
(Rev 6).
Additional Notes (previous releases)
1 | Information in this spreadsheet is taken from the following sources. The data from each of these sources are
contained on a separate tab within this spreadsheet.
| Code | Title | Relevance
| 90.1-2010 | ASHRAE Standard 90.1-2010 | Baseline for LEED 2012
| 90.1-2007 | ASHRAE Standard 90.1-2007 | Baseline for LEED 2.2
| 90.1-2001 | ASHRAE Standard 90.1-2001 | Baseline for IRS 179D
| NREL956 | Methodology for Modeling . ., NREL 550-41956 | Data for plug loads and other assumptions
| ACM05 | California 2005 ACM Manual | Referenced by IRS 179D
| CEUS-2003 | California Energy Utilization Survey, Iron, 2006 | Data source for refrigeration and cooking power
| ECB-CS | Unpublished ECB Compliance Supplement | Data source
2 | The list for the table in the main tab "Modeling Data" is consistent with ASHRAE 90.1-2010. All the data is mapped
to these buildings and space types in the tab titled "Mapping".
3 | The data in the "Modeling Data" tab is automatically looked up from the source tables based on information on the
"Mapping" tab. Changes should be made here, not on the "Modeling Data" tab. The exception is for the schedules
columns, which are not automatically looked up.
4 | The data in "Modeling Data (Rev 6)" is legacy information for comparison to the revised information contained in
"Modeling Data".

## Mapping (hidden)
COMNET List - Names from 2016 PRM | Mapping to 90.1-2016 PRM | Mapping to 90.1-2010 | Mapping to 90.1-2007 | Mapping to 90.1-2001 | Mapping to SSPC-90.1 | Mapping to CBECS 2003 | Mapping to CEUS | Mapping to ECB-CS | Mapping to ACM05
BA Automotive Facility | BA Automotive Facility | BA Automotive Facility | BA Automotive facility | BA Automotive Facility | Automotive Facility | Service (except Food) Vehicle service/repair shop | Miscellaneous | CS Auto repair | SO Auto Repair
BA Convention Center | BA Convention Center | BA Convention Center | BA Convention center | BA Convention Center | Convention Center | Public assembly PBA | Assembly | BA Assembly | BA Convention Centers
BA Courthouse | BA Courthouse | BA Courthouse | BA Courthouse | BA Court House | Courthouse | Office Government office | Large Office | BA Health & Institutional | BA Convention Centers
BA Dining: Bar Lounge/Leisure | BA Dining: Bar Lounge/Leisure | BA Dining: Bar Lounge/Leisure | BA Dining: bar lounge/leisure | BA Dining: Bar Lounge/Leisure | Dining: Bar/Lounge/Leisure | Food service Other food service | Restaurant | BA Food Service | BA Restaurants
BA Dining: Cafeteria/Fast Food | BA Dining: Cafeteria/Fast Food | BA Dining: Cafeteria/Fast Food | BA Dining: cafeteria/fast food | BA Dining: Cafeteria/Fast Food | Dining: Cafeteria/Fast Food | Food service Fast food | Restaurant | BA Food Service | BA Restaurants
BA Dining: Family | BA Dining: Family | BA Dining: Family | BA Dining: family | BA Dining: Family | Dining: Family | Food service Restaurant/cafeteria | Restaurant | BA Food Service | BA Restaurants
BA Dormitory | BA Dormitory | BA Dormitory | BA Dormitory | BA Dormitory | Dormitory | Lodging Dormitory/fraternity/sorority | Lodging | BA Lodging | SO Hotel/Motel Guest Room
BA Exercise Center | BA Exercise Center | BA Exercise Center | BA Exercise center | BA Exercise Center | Exercise Center | Public assembly Recreation | Assembly | BA Health & Institutional | SO All Others
BA Fire Station | BA Fire Station | BA Fire Station | BA Police/fire station | BA Police/Fire Station | Fire Station | Public order and safety Fire station/police station | Miscellaneous | BA Office (Business) | SO Police Station and Fire Station
BA Gymnasium | BA Gymnasium | BA Gymnasium | BA Gymnasium | BA Gymnasium | Gymnasium | Public assembly Recreation | Assembly | BA Health & Institutional | SO Exercise, Center, Gymnasium
BA Healthcare Clinic | BA Healthcare Clinic | BA Healthcare Clinic | BA Health-care clinic | BA Hospital/Health Care | Health-Care Clinic | Outpatient health care PBA | Health | BA Health & Institutional | BA Medical Buildings and Clinics
BA Hospital | BA Hospital | BA Hospital | BA Hospital | BA Hospital/Health Care | Hospital | Inpatient health care PBA | Health | BA Health & Institutional | BA Medical Buildings and Clinics
BA Hotel | BA Hotel/Motel | BA Hotel | BA Hotel | BA Hotel | Hotel | Lodging Hotel | Lodging | BA Lodging | SO Hotel/Motel Guest Room
BA Library | BA Library | BA Library | BA Library | BA Library | Library | Public assembly Library | Small Office | BA Educational | BA Library
BA Manufacturing Facility | BA Manufacturing Facility | BA Manufacturing Facility | BA Manufacturing facility | BA Manufacturing Facility | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Miscellaneous | BA Industrial | BA General Commercial and Industrial Work Buildings, High Bay
BA Motel | BA Hotel/Motel | BA Motel | BA Motel | BA Motel | Motel | Lodging Hotel | Lodging | BA Lodging | SO Hotel/Motel Guest Room
BA Motion Picture Theater | BA Motion Picture Theater | BA Motion Picture Theater | BA Motion picture theater | BA Motion Picture Theater | Motion Picture Theater | Public assembly Entertainment/culture | Assembly | BA Assembly | SO Auditorium
BA Multifamily | BA Multifamily | BA Multifamily | BA Multifamily | BA Multi-Family | Multifamily | Lodging Other lodging | Lodging | SS General Dormitory | SO High-Rise Residential Living Spaces
BA Museum | BA Museum | BA Museum | BA Museum | BA Museum | Museum | Public assembly Entertainment/culture | Assembly | BA Assembly | SO Exhibit, Museum
BA Office | BA Office | BA Office | BA Office | BA Office | Office | Office PBA | All Offices | BA Office (Business) | BA Office Buildings
BA Parking Garage | BA Parking Garage | BA Parking Garage | BA Parking garage | BA Parking Garage | Parking Garage | No default | Unrefrigerated Warehouse | SS Garage Parking garage | SO All Others
BA Penitentiary | BA Penitentiary | BA Penitentiary | BA Penitentiary | BA Penitentiary | Penitentiary | Public order and safety Other public order and safety | Lodging | BA Lodging | SO Hotel/Motel Guest Room
BA Performing Arts Theater | BA Performing Arts Theater | BA Performing Arts Theater | BA Performing arts theater | BA Performing Arts Theater | Performing Arts Theater | Public assembly Entertainment/culture | Assembly | BA Assembly | SO Theater, Performance
BA Police Station | BA Police Station | BA Police Station | BA Police/fire station | BA Police/Fire Station | Police Station | Public order and safety Fire station/police station | Miscellaneous | BA Office (Business) | SO Police Station and Fire Station
BA Post Office | BA Post Office | BA Post Office | BA Post office | BA Post Office | Post Office | Service (except Food) Post office/postal center | Miscellaneous | BA Office (Business) | SO General Commercial and Industrial Work, Low Bay
BA Religious Building | BA Religious Building | BA Religious Building | BA Religious building | BA Religious Building | Religious Building | Religious worship PBA | Assembly | BA Assembly | BA Religious Facilities
BA Retail | BA Retail | BA Retail | BA Retail | BA Retail | Retail | Retail (except Malls) PBA | Retail | BA Retail | SO Retail Merchandise Sales, Wholesale Showroom
BA School/University | BA School/University | BA School/University | BA School/university | BA School/University | School/University | Education PBA | School | BA Educational | BA Classroom Building
BA Sports Arena | BA Sports Arena | BA Sports Arena | BA Sports arena | BA Sports Arena | Sports Arena | Public assembly PBA | Assembly | BA Assembly | BA Auditoriums
BA Town Hall | BA Town Hall | BA Town Hall | BA Town hall | BA Town Hall | Town Hall | Public assembly PBA | All Offices | BA Assembly | BA Office Buildings
BA Transportation | BA Transportation | BA Transportation | BA Transportation | BA Transportation | Transportation | Service (except Food) Other service | Assembly | SS Transport Terminal- concourse | SO Transportation Function
BA Warehouse | BA Warehouse | BA Warehouse | BA Warehouse | BA Warehouse | Warehouse | Nonrefrigerated warehouse Non-refrigerated warehouse | Unrefrigerated Warehouse | BA Warehouse (Storage) | SO Commercial and Industrial Storage (conditioned or unconditioned)
BA Workshop | BA Workshop | BA Workshop | BA Workshop | BA Workshop | Workshop | Service (except Food) Repair shop | Miscellaneous | BA Industrial | BA General Commercial and Industrial Work Buildings, Low Bay
COMNET List - Names from 2016 PRM | Mapping to 90.1-2016 PRM | Mapping to 90.1-2010 | Mapping to 90.1-2007 | Mapping to 90.1-2001 | Mapping to SSPC-90.1 | Mapping to CBECS 2003 | Mapping to CEUS | Mapping to ECB-CS | Mapping to ACM05
CS Audience Seating Area, Auditorium | CS Audience Seating Area, Auditorium | CS Audience Seating Permanent Auditorium | CS Audience/Seating Area General | CS Audience/Seating Area General | Performing Arts Theater | Public assembly PBA | Assembly | SS Theater Auditorium seating area | SO Auditorium
CS Audience Seating Area, Convention Center | CS Audience Seating Area, Convention Center | SS Convention Center Audience Seating | CS Audience/Seating Area Convention Center | SS Audience/Seating Area Convention Center | Convention Center | Public assembly PBA | Assembly | CS Conf./mtg./multi-use | SO Convention, Conference, Multi-purpose and Meeting Centers (Note 10)
CS Audience Seating Area, Exercise Center | CS Audience Seating Area, Exercise Center | SS Gymnasium/Fitness Center Gymnasium Audience Seating | CS Audience/Seating Area Exercise Center | SS Audience/Seating Area Exercise Center | Exercise Center | Public assembly Recreation | Assembly | SS Sports Indoor athletics seating | SO Exercise, Center, Gymnasium
CS Audience Seating Area, Gymnasium | CS Audience Seating Area, Gymnasium | SS Gymnasium/Fitness Center Gymnasium Audience Seating | CS Audience/Seating Area Gymnasium | SS Audience/Seating Area Gymnasium | Gymnasium | Public assembly Recreation | Assembly | SS Sports Indoor athletics seating | SO Exercise, Center, Gymnasium
CS Audience Seating Area, Motion Picture Theater | CS Audience Seating Area, Motion Picture Theater | CS Audience Seating Permanent Motion Picture Theater | CS Audience/Seating Area Motion Picture Theater | SS Audience/Seating Area Motion Picture Theater | Motion Picture Theater | Public assembly Entertainment/culture | Assembly | SS Theater Motion picture seating | SO Theater, Motion Picture
CS Audience Seating Area, Penitentiary | CS Audience Seating Area, Penitentiary | CS Audience Seating Permanent Auditorium | CS Audience/Seating Area Penitentiary | SS Audience/Seating Area Penitentiary | Penitentiary | Public assembly PBA | Assembly | SS Theater Auditorium seating area | SO Auditorium
CS Audience Seating Area, Performing Arts Theater | CS Audience Seating Area, Performing Arts Theater | CS Audience Seating Permanent Performing Arts Theater | CS Audience/Seating Area Performing Arts Theater | SS Audience/Seating Area Performing Arts Theater | Performing Arts Theater | Public assembly Entertainment/culture | Assembly | SS Theater Performing arts seating | SO Theater, Performance
CS Audience Seating Area, Religious Building | CS Audience Seating Area, Religious Building | SS Religious Buildings Audience Seating | CS Audience/Seating Area Religious Buildings | SS Audience/Seating Area Religious Buildings | Religious Building | Public assembly Social/meeting | Assembly | SS Religious Worship- congregation | SO Religious Worship
CS Audience Seating Area, Sports Arena | CS Audience Seating Area, Sports Arena | SS Sports Arena Audience Seating | CS Audience/Seating Area Sports Arena | SS Audience/Seating Area Sports Arena | Sports Arena | Public assembly Entertainment/culture | Assembly | SS Sports Indoor athletics seating | SO Exercise, Center, Gymnasium
CS Audience Seating Area, Transportation Facility | CS Audience Seating Area, Transportation Facility | SS Transportation Audience Seating | CS Audience/Seating Area Transportation | SS Audience/Seating Area Transportation | Transportation | Public assembly PBA | Assembly | SS Transport Terminal- waiting/lounge | SO Transportation Function
CS Audience Seating Area, Other | CS Audience Seating Area, Other | CS Audience Seating Permanent Auditorium | CS Audience/Seating Area General | CS Audience/Seating Area General | Use Whole Building Data | Public assembly PBA | Assembly | SS Theater Auditorium seating area | SO Auditorium
CS Atrium, Less than or equal to 40 ft | CS Atrium, Less than or equal to 40 ft | CS Atrium First 40 ft in Height | CS Atrium—First Three Floors | CS Atrium—First Three Floors | Use Whole Building Data | No default | Assembly | CS Atria- 1st three floors | SO Malls and Atria
CS Atrium, More than 40 ft | CS Atrium, More than 40 ft | CS Atrium Height Above 40 ft | CS Atrium—Each Additional Floor | CS Atrium—Each Additional Floor | Use Whole Building Data | No default | Assembly | CS Atria- 1st three floors | SO Malls and Atria
CS Banking Activity Area, | CS Banking Activity Area, | SS Bank/Office Banking Activity Area | SS Bank/Office Banking Activity Area | SS Bank/Office Banking Activity Area | Office | Office Bank/other financial | All Offices | CS Banking activity | BA Financial Institutions
CS Classroom/Lecture/Training, Penitentiary | CS Classroom/Lecture/Training, Penitentiary | CS Classroom/Lecture/Training | CS Classroom/Lecture/Training General | CS Classroom/Lecture/Training General | Penitentiary | Education Other classroom education | School | CS Classroom/lecture/training | SO Classrooms, Lecture, Training, Vocational Room
CS Classroom/Lecture/Training, K-12, laboratory and shops | CS Classroom/Lecture/Training, K-12, laboratory and shops | CS Classroom/Lecture/Training | CS Classroom/Lecture/Training General | CS Classroom/Lecture/Training General | School/University | Education Other classroom education | School | CS Classroom/lecture/training | SO Classrooms, Lecture, Training, Vocational Room
CS Classroom/Lecture/Training, Other | CS Classroom/Lecture/Training, Other | CS Classroom/Lecture/Training | CS Classroom/Lecture/Training General | CS Classroom/Lecture/Training General | Use Whole Building Data | Education Other classroom education | School | CS Classroom/lecture/training | SO Classrooms, Lecture, Training, Vocational Room
CS Conference/Meeting/Multipurpose, | CS Conference/Meeting/Multipurpose, | CS Conference/Meeting/Multipurpose | CS Conference/Meeting/Multipurpose | CS Conference/Meeting/Multipurpose | Use Whole Building Data | Public assembly Social/meeting | College | CS Conf./mtg./multi-use | SO Convention, Conference, Multi-purpose and Meeting Centers (Note 10)
CS Confinment Cells, | CS Confinment Cells, | SS Courthouse/Police Station/Penitentiary Confinement Cells | SS Courthouse/Police Station/Penitentiary Confinement Cells | SS Courthouse/Police Station/Penitentiary Confinement Cells | Penitentiary | Public order and safety Other public order and safety | Lodging | SS Civil Services Jail/peniten. living area | SO Police Station and Fire Station
CS Copy/Print Room, | CS Copy/Print Room, | CS Workshop, General | CS Workshop |  | Use Whole Building Data | Use whole building data | No default | No default | No default
CS Corridor, Assisted Living | CS Corridor, Assisted Living | CS Corridor/Transition |  |  | Use Whole Building Data | Nursing Nursing home/assisted living | Lodging | SS Health Corridors- Health | SO Corridors, Restrooms, Stairs, and Support Areas
CS Corridor, Hospital | CS Corridor, Hospital | SS Hospital Corridor/Transition | CS Corridor/Transition Hospital | SS Corridor/Transition Hospital | Use Whole Building Data | Inpatient health care Hospital/inpatient health | Health | SS Health Corridors- Health | SO Corridors, Restrooms, Stairs, and Support Areas
CS Corridor, Manufacturing | CS Corridor, Manufacturing | SS Manufacturing Corridor/Transition | CS Corridor/Transition Manufacturing Facility | SS Corridor/Transition Manufacturing Facility | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Assembly | CS Corridor/transition | SO Corridors, Restrooms, Stairs, and Support Areas
CS Corridor, Other | CS Corridor, Other | CS Corridor/Transition | CS Corridor/Transition General | CS Corridor/Transition General | Use Whole Building Data | Use whole building data | Assembly | CS Corridor/transition | SO Corridors, Restrooms, Stairs, and Support Areas
CS Courtroom, | CS Courtroom, | SS Courthouse/Police Station/Penitentiary Courtroom | SS Courthouse/Police Station/Penitentiary Courtroom | SS Courthouse/Police Station/Penitentiary Courtroom | Courthouse | Public order and safety Other public order and safety | Large Office | SS Civil Services Courtroom | SO Police Station and Fire Station
CS Computer Room, | CS Computer Room, | SS Manufacturing Equipment Room | SS Manufacturing Equipment Room | SS Manufacturing Equipment Room | No default | No default | No default | No default | SO All Others
CS Dining Area, Penitentiary | CS Dining Area, Penitentiary | BA Dining: Cafeteria/Fast Food | BA Dining: cafeteria/fast food | BA Dining: Cafeteria/Fast Food | Dining: Cafeteria/Fast Food | Food service Restaurant/cafeteria | Restaurant | SS Food Cafeteria/fast food | SO Dining
CS Dining Area, Assisted Living | CS Dining Area, Assisted Living | BA Dining: Family | BA Dining: family | BA Dining: Family | Dining: Cafeteria/Fast Food | Food service Other food service | Restaurant | SS Food Bar/lounge | SO Dining
CS Dining Area, Bar Lounge/Leisure | CS Dining Area, Bar Lounge/Leisure | CS Dining Area Bar Lounge/Leisure Dining | CS Dining Area Bar Lounge/Leisure Dining | SS Dining Area Bar Lounge/Leisure Dining | Dining: Bar/Lounge/Leisure | Food service Restaurant/cafeteria | Restaurant | SS Food Bar/lounge | SO Bar, Cocktail Lounge and Casino
CS Dining Area, Cafeteria or Fast Food | CS Dining Area, Cafeteria or Fast Food | BA Dining: Cafeteria/Fast Food | BA Dining: cafeteria/fast food | BA Dining: Cafeteria/Fast Food | Dining: Cafeteria/Fast Food | Food service Fast food | Restaurant | SS Food Cafeteria/fast food | SO Dining
CS Dining Area, Family Dining | CS Dining Area, Family Dining | CS Dining Area Family Dining | CS Dining Area Family Dining | SS Dining Area Family Dining | Dining: Family | Food service Other food service | Restaurant | SS Food Family dining | SO Corridors, Restrooms, Stairs, and Support Areas
CS Dining Area, Other | CS Dining Area, Other | CS Dining Area General | CS Dining Area General | CS Dining Area General | Dining: Family | Food service Other food service | Restaurant | CS Dining area- General | SO Dining
CS Electrical/Mechanical , | CS Electrical/Mechanical , | CS Electrical/Mechanical | CS Electrical/Mechanical | CS Electrical/Mechanical | No default | Use whole building data | Use whole building data | Use whole building data | SO Electrical, Mechanical Room
CS Emergency Vehicle Garage, | CS Emergency Vehicle Garage, | CS Electrical/Mechanical | CS Electrical/Mechanical | CS Electrical/Mechanical | Use Whole Building Data | Vacant PBA | Miscellaneous | CS Mechanical/electrical | SO Police Station and Fire Station
CS Food Preparation , | CS Food Preparation , | CS Food Preparation | CS Food Preparation | CS Food Preparation | Use Whole Building Data | Food service Other food service | Food Preparation | CS Food preparation | SO Kitchen, Food Preparation
CS Guest Room, | CS Guest Room, | SS Hotel/Highway Lodging Hotel Guest Rooms | SS Hotel/Motel Guest Rooms | SS Hotel/Motel Guest Rooms | Hotel | Lodging Hotel | Lodging | SS General Guest rooms | SO Hotel/Motel Guest Room
CS Judges Chambers, | CS Judges Chambers, | SS Courthouse/Police Station/Penitentiary Judges’ Chambers | SS Courthouse/Police Station/Penitentiary Judges’ Chambers | SS Courthouse/Police Station/Penitentiary Judges’ Chambers | Office | Public order and safety Other public order and safety | Large Office | CS Office - enclosed | SO Office (Greater than 250 square feet in floor area)
CS Laboratory, Classrooms | CS Laboratory, Classrooms | CS Laboratory Classrooms | CS Classroom/Lecture/Training General | CS Classroom/Lecture/Training General | Use Whole Building Data | Laboratory PBA | College | CS Classroom/lecture/training | SO Classrooms, Lecture, Training, Vocational Room
CS Laboratory, Other | CS Laboratory, Other | CS Laboratory Medical/Industrial/Research | CS Laboratory | SS Laboratory | No default | Laboratory PBA | No default | CS Laboratory/research | SO Laboratory, Scientific
CS Laundry/Washing Area, | CS Laundry/Washing Area, | SS Hospital Laundry/Washing | SS Hospital Laundry—Washing | SS Hospital Laundry—Washing | No default | Service (except Food) Other service | No default | CS Washing | SO Laundry
CS Loading Dock, Interior, | CS Loading Dock, Interior, | SS Warehouse Medium/Bulky Material Storage | SS Warehouse Medium/Bulky Material Storage | SS Warehouse Medium/Bulky Material Storage | Warehouse | No default | Unrefrigerated Warehouse | SS Warehouse Medium/Bulky material | SO Commercial and Industrial Storage (conditioned or unconditioned)
CS Lobby, Assisted Living | CS Lobby, Assisted Living | CS Lobby General | CS Lobby General | CS Lobby All Other | Hotel | Nursing Nursing home/assisted living | Lodging | SS Hotels Lobby-Hotel | SO Lobby, Hotel
CS Lobby, Elevator | CS Lobby, Elevator | CS Lobby Elevator | CS Lobby General | CS Lobby All Other | Use Whole Building Data | Use whole building data | Assembly | CS Lobby | SO Lobby, Main Entry
CS Lobby, Hotel | CS Lobby, Hotel | SS Hotel/Highway Lodging Hotel Lobby | CS Lobby Hotel | SS Lobby Hotel | Hotel | Lodging Hotel | Assembly | SS Hotels Lobby-Hotel | SO Lobby, Hotel
CS Lobby, Motion Picture Theater | CS Lobby, Motion Picture Theater | CS Lobby Motion Picture Theater | CS Lobby Motion Picture Theater | SS Lobby Motion Picture Theater | Motion Picture Theater | Public assembly Entertainment/culture | Assembly | SS Theater Lobby - other theaters | SO Lobby, Main Entry
CS Lobby, Performing Arts Theater | CS Lobby, Performing Arts Theater | CS Lobby Performing Arts Theater | CS Lobby Performing Arts Theater | SS Lobby Performing Arts Theater | Performing Arts Theater | Public assembly Entertainment/culture | Assembly | SS Theater Lobby - Performing Arts | SO Lobby, Main Entry
CS Lobby, Other | CS Lobby, Other | CS Lobby General | CS Lobby General | CS Lobby All Other | Use Whole Building Data | Use whole building data | Assembly | CS Lobby | SO Lobby, Main Entry
CS Locker Room , | CS Locker Room , | CS Locker Room | CS Dressing/Locker/Fitting Room | SS Dressing/Locker/Fitting Room | No default | No default | Miscellaneous | CS Dressing/locker/fitting | SO All Others
CS Lounge/Break, Healthcare | CS Lounge/Break, Healthcare | SS Hospital Lounge/Recreation | CS Lounge/Recreation Hospital | CS Lounge/Recreation | Use Whole Building Data | Inpatient health care Hospital/inpatient health | Assembly | SS Health Reception/waiting | SO Waiting Area
CS Lounge/Break, Other | CS Lounge/Break, Other | CS Lounge/Recreation | CS Lounge/Recreation General | CS Lounge/Recreation | Use Whole Building Data | Use whole building data | Assembly | CS Lounge/recreation | SO Lounge, Recreation
CS Office, Enclosed | CS Office, Enclosed | CS Office Enclosed | CS Office Enclosed | CS Office Enclosed | Office | Office PBA | All Offices | CS Office - enclosed | SO Office (250 square feet in floor area or less)
CS Office, Open Plan | CS Office, Open Plan | CS Office Open Plan | CS Office Open Plan | CS Office Open Plan | Office | Office PBA | All Offices | CS Office - open | SO Office (Greater than 250 square feet in floor area)
CS Parking Area, Interior, | CS Parking Area, Interior, | SS Parking Garage Garage Area | SS Parking Garage Garage Area | SS Parking Garage Pedestrian | Parking Garage | No default | Unrefrigerated Warehouse | SS Garage Parking garage | SO All Others
CS Pharmacy Area, | CS Pharmacy Area, | SS Hospital Pharmacy | SS Hospital Pharmacy | SS Hospital Pharmacy | Retail | Retail (except Malls) Retail store | Retail | SS Health Nurse station/Pharmacy | SO Retail Merchandise Sales, Wholesale Showroom
CS Restrooms , Assisted Living | CS Restrooms , Assisted Living | CS Restrooms | CS Restrooms | CS Restrooms | Hotel | Nursing Nursing home/assisted living | Lodging | CS Restrooms | SO Corridors, Restrooms, Stairs, and Support Areas
CS Restrooms , Other | CS Restrooms , Other | CS Restrooms | CS Restrooms | CS Restrooms | Use Whole Building Data | Use whole building data | Use whole building data | CS Restrooms | SO Corridors, Restrooms, Stairs, and Support Areas
CS Sales Area, | CS Sales Area, | SS Retail Sales Area | SS Retail Sales Area | SS Retail Sales Area | Retail | Retail (except Malls) Retail store | Retail | SS Retail Department store | SO Retail Merchandise Sales, Wholesale Showroom
CS Seating Area General, | CS Seating Area General, | CS Audience Seating Permanent Auditorium | CS Audience/Seating Area General | CS Audience/Seating Area General | Use Whole Building Data | Use whole building data | Use whole building data | Use whole building data | Use whole building data
CS Stairway, | CS Stairway, | CS Stairway | CS Stairs—Active | CS Stairs—Active | Use Whole Building Data | Use whole building data | Use whole building data | CS Stairs- active | SO Corridors, Restrooms, Stairs, and Support Areas
CS Storage, Hospital | CS Storage, Hospital | SS Hospital Medical Supply | SS Hospital Medical Supply | SS Hospital Medical Supply | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Medical supplies | SO Medical and Clinical Care
CS Storage, >= 50 ft² | CS Storage, >= 50 ft² | CS Storage | CS Inactive Storage General | CS Inactive Storage General | Warehouse | Nonrefrigerated warehouse PBA | Unrefrigerated Warehouse | CS Active storage | SO Commercial and Industrial Storage (conditioned or unconditioned)
CS Storage, < 50 ft² | CS Storage, < 50 ft² | CS Storage | CS Active Storage General | CS Active Storage General | Warehouse | Nonrefrigerated warehouse PBA | Unrefrigerated Warehouse | CS Inactive storage | SO Commercial and Industrial Storage (conditioned or unconditioned)
CS Vehicular Maintenance, | CS Vehicular Maintenance, | SS Automotive Service/Repair | SS Automotive Service Repair | SS Automotive Service Repair | Automotive Facility | Service (except Food) Vehicle service/repair shop | Miscellaneous | CS Auto repair | SO Auto Repair
CS Workshop, | CS Workshop, | CS Workshop, General | CS Workshop | SS Manufacturing Workshop | Workshop | Service (except Food) Repair shop | Miscellaneous | SS Manufacture General workshop | SO General Commercial and Industrial Work, Precision
SS Assisted Living, Chapel | SS Assisted Living, Chapel | BA Religious Building | BA Religious building | BA Religious Building | Hotel | Nursing Nursing home/assisted living | Lodging | SS General Recep./waiting/prefunc. | SO Housing, Public and Common Areas: Multi-family, Dormitory
SS Assisted Living, Recreation Room | SS Assisted Living, Recreation Room | CS Lounge/Recreation | CS Lounge/Recreation General | CS Lounge/Recreation | Hotel | Nursing Nursing home/assisted living | Lodging | CS Lounge/recreation | SO Lounge, Recreation
SS Convention Center, Exhibit Space | SS Convention Center, Exhibit Space | SS Convention Center Exhibit Space | SS Convention Center Exhibit Space | SS Convention Center Exhibit Space | Convention Center | Public assembly PBA | Assembly | SS Exhibition Hall Exhibit space | SO Convention, Conference, Multi-purpose and Meeting Centers (Note 10)
SS Dormitory, Living Quarters | SS Dormitory, Living Quarters | SS Dormitory Living Quarters | SS Dormitory Living Quarters | SS Dormitory Living Quarters | Hotel | Lodging Dormitory/fraternity/sorority | Lodging | SS General Dormitory | SO Housing, Public and Common Areas: Multi-family, Dormitory
SS Fire Station, Sleeping Quarters | SS Fire Station, Sleeping Quarters | SS Fire Stations Sleeping Quarters | SS Fire Stations Sleeping Quarters | SS Fire Stations Sleeping Quarters | Fire Station | Public order and safety Fire station/police station | Lodging | SS General Dormitory | SO Housing, Public and Common Areas: Multi-family, Dormitory
SS Gymnasium/Fitness Center, Exercise Area | SS Gymnasium/Fitness Center, Exercise Area | SS Gymnasium/Fitness Center Fitness Area | SS Gymnasium/Exercise Center Exercise Area | SS Gymnasium/Exercise Center Exercise Area | Exercise Center | Public assembly Recreation | Assembly | SS Sports Exercise area | SO Exercise, Center, Gymnasium
SS Gymnasium/Fitness Center, Playing Area | SS Gymnasium/Fitness Center, Playing Area | SS Gymnasium/Fitness Center Playing Area | SS Gymnasium/Exercise Center Playing Area | SS Gymnasium/Exercise Center Playing Area | Exercise Center | Public assembly Recreation | Assembly | SS Sports Gymnasium playing area | SO Exercise, Center, Gymnasium
SS Healthcare, Emergency Room | SS Healthcare, Emergency Room | SS Hospital Emergency | SS Hospital Emergency | SS Hospital Emergency | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Surgery/emergency/OB | SO Medical and Clinical Care
SS Healthcare, Exam/Treatment | SS Healthcare, Exam/Treatment | SS Hospital Exam/Treatment | SS Hospital Exam/Treatment | SS Hospital Exam/Treatment | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Examination | SO Medical and Clinical Care
SS Healthcare, Supply Room | SS Healthcare, Supply Room | SS Hospital Medical Supply | SS Hospital Medical Supply | SS Hospital Medical Supply | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Medical supplies | SO Medical and Clinical Care
SS Healthcare, Nursery | SS Healthcare, Nursery | SS Hospital Nursery | SS Hospital Nursery | SS Hospital Nursery | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Patient rooms/nursery | SO Medical and Clinical Care
SS Healthcare, Nurses’ Station | SS Healthcare, Nurses’ Station | SS Hospital Nurses’ Station | SS Hospital Nurses’ Station | SS Hospital Nurses’ Station | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Nurse station/Pharmacy | SO Medical and Clinical Care
SS Healthcare, Operating Room | SS Healthcare, Operating Room | SS Hospital Operating Room | SS Hospital Operating Room | SS Hospital Operating Room | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Surgery/emergency/OB | SO Medical and Clinical Care
SS Healthcare, Patient Room | SS Healthcare, Patient Room | SS Hospital Patient Room | SS Hospital Patient Room | SS Hospital Patient Room | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Patient rooms/nursery | SO Medical and Clinical Care
SS Healthcare, Physical Therapy | SS Healthcare, Physical Therapy | SS Hospital Physical Therapy | SS Hospital Physical Therapy | SS Hospital Physical Therapy | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Therapy | SO Medical and Clinical Care
SS Healthcare, Recovery Room | SS Healthcare, Recovery Room | SS Hospital Recovery | SS Hospital Recovery | SS Hospital Recovery | Hospital | Inpatient health care Hospital/inpatient health | Health | SS Health Recovery | SO Medical and Clinical Care
SS Library, Reading Area | SS Library, Reading Area | SS Library Reading Area | SS Library Reading Area | SS Library Reading Area | Library | Public assembly Library | Assembly | SS Library Reading area | SO Library, Reading Areas
SS Library, Stacks | SS Library, Stacks | SS Library Stacks | SS Library Stacks | SS Library Stacks | Library | Public assembly Library | Assembly | SS Library Stacks | SO Library, Stacks
SS Manufacturing Facility, Detailed Manufacturing | SS Manufacturing Facility, Detailed Manufacturing | SS Manufacturing Detailed Manufacturing | SS Manufacturing Detailed Manufacturing | SS Manufacturing Detailed Manufacturing | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Miscellaneous | SS Manufacture General manufacturing | SO General Commercial and Industrial Work, Precision
SS Manufacturing Facility, Equipment Room | SS Manufacturing Facility, Equipment Room | SS Manufacturing Equipment Room | SS Manufacturing Equipment Room | SS Manufacturing Equipment Room | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Miscellaneous | SS Manufacture Equipment room | BA General Commercial and Industrial Work Buildings, High Bay
SS Manufacturing Facility, Extra High Bay (>50 ft Floor to Ceiling Height) | SS Manufacturing Facility, Extra High Bay (>50 ft Floor to Ceiling Height) | SS Manufacturing Extra High Bay (>50 ft Floor to Ceiling Height) | SS Manufacturing High Bay (³25 ft Floor to Ceiling Height) | SS Manufacturing High Bay (³25 ft Floor to Ceiling Height) | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Miscellaneous | SS Manufacture General manufacturing | BA General Commercial and Industrial Work Buildings, High Bay
SS Manufacturing Facility, High Bay (25–50 ft Floor to Ceiling Height) | SS Manufacturing Facility, High Bay (25–50 ft Floor to Ceiling Height) | SS Manufacturing High Bay (25–50 ft Floor to Ceiling Height) | SS Manufacturing High Bay (³25 ft Floor to Ceiling Height) | SS Manufacturing High Bay (³25 ft Floor to Ceiling Height) | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Miscellaneous | SS Manufacture General manufacturing | BA General Commercial and Industrial Work Buildings, High Bay
SS Manufacturing Facility, Low Bay (<25 ft Floor to Ceiling Height) | SS Manufacturing Facility, Low Bay (<25 ft Floor to Ceiling Height) | SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height) | SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height) | SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height) | Manufacturing Facility | Nonrefrigerated warehouse Distribution/shipping center | Miscellaneous | SS Manufacture General manufacturing | BA General Commercial and Industrial Work Buildings, High Bay
SS Museum, General Exhibition | SS Museum, General Exhibition | SS Museum General Exhibition | SS Museum General Exhibition | SS Museum General Exhibition | Museum | Public assembly Entertainment/culture | Assembly | SS Museum General exhibition | SO Exhibit, Museum
SS Museum, Restoration | SS Museum, Restoration | SS Museum Restoration | SS Museum Restoration | SS Museum Restoration | Museum | Service (except Food) Repair shop | Miscellaneous | SS Museum Restoration | SO Commercial and Industrial Storage (conditioned or unconditioned)
SS Post Office, Sorting Area | SS Post Office, Sorting Area | SS Post Office Sorting Area | SS Post Office—Sorting Area | SS Post Office Sorting Area | Post Office | Office Government office | Small Office | SS Manufacture General manufacturing | BA Office Buildings
SS Religious Building, Fellowship Hall | SS Religious Building, Fellowship Hall | SS Religious Buildings Fellowship Hall | SS Religious Buildings Fellowship Hall | SS Religious Buildings Fellowship Hall | Religious Building | Religious worship PBA | Assembly | SS Religious Worship- congregation | SO Religious Worship
SS Religious Building, Worship/Pulpit/Choir | SS Religious Building, Worship/Pulpit/Choir | SS Religious Buildings Worship Pulpit, Choir | SS Religious Buildings Worship Pulpit, Choir | SS Religious Buildings Worship Pulpit, Choir | Religious Building | Religious worship PBA | Assembly | SS Religious Worship- pulpit, choir | SO Religious Worship
SS Retail, Dressing/Fitting Room | SS Retail, Dressing/Fitting Room | CS Dressing/Fitting Room Performing Arts Theater | CS Dressing/Locker/Fitting Room | SS Dressing/Locker/Fitting Room | Retail | Retail (except Malls) Other retail | Miscellaneous | CS Dressing/locker/fitting | SO Retail Merchandise Sales, Wholesale Showroom
SS Retail, Mall Concourse | SS Retail, Mall Concourse | SS Retail Mall Concourse | SS Retail Mall Concourse | SS Retail Mall Concourse | Retail | Enclosed mall PBA | Retail | SS Retail Mall concourse | SO Malls and Atria
SS Sports Arena Playing Area, Class I | SS Sports Arena Playing Area, Class I | SS Sports Arena Court Sports Arena—Class 1 | SS Sports Arena Court Sports Area | SS Sports Arena Court Sports Area | Sports Arena | Public assembly Recreation | Assembly | SS Sports Gymnasium playing area | SO Exercise, Center, Gymnasium
SS Sports Arena Playing Area, Class II | SS Sports Arena Playing Area, Class II | SS Sports Arena Court Sports Arena—Class 2 | SS Sports Arena Court Sports Area | SS Sports Arena Court Sports Area | Sports Arena | Public assembly Recreation | Assembly | SS Sports Jai-alai/tennis/hockey | SO Exercise, Center, Gymnasium
SS Sports Arena Playing Area, Class III | SS Sports Arena Playing Area, Class III | SS Sports Arena Court Sports Arena—Class 3 | SS Sports Arena Court Sports Area | SS Sports Arena Court Sports Area | Sports Arena | Public assembly Recreation | Assembly | SS Sports Jai-alai/tennis/hockey | SO Exercise, Center, Gymnasium
SS Sports Arena Playing Area, Class IV | SS Sports Arena Playing Area, Class IV | SS Sports Arena Court Sports Arena—Class 4 | SS Sports Arena Court Sports Area | SS Sports Arena Court Sports Area | Sports Arena | Public assembly Recreation | Assembly | SS Sports Jai-alai/tennis/hockey | SO Exercise, Center, Gymnasium
SS Transportation, Baggage/Carousel Area | SS Transportation, Baggage/Carousel Area | SS Transportation Air/Train/Bus—Baggage Area | SS Transportation Air/Train/Bus—Baggage Area | SS Transportation Air/Train/Bus—Baggage Area | Transportation | Public assembly Other public assembly | Assembly | SS Transport Terminal- baggage | SO Transportation Function
SS Transportation, Concourse | SS Transportation, Concourse | SS Transportation Airport—Concourse | SS Transportation Airport—Concourse | SS Transportation Airport—Concourse | Transportation | Public assembly Other public assembly | Assembly | SS Transport Terminal- concourse | SO Transportation Function
SS Transportation, Ticket Counter | SS Transportation, Ticket Counter | SS Transportation Terminal—Ticket Counter | SS Transportation Terminal—Ticket Counter | SS Transportation Terminal—Ticket Counter | Transportation | Public assembly Other public assembly | Assembly | SS Transport Terminal- ticket counter | SO Transportation Function
SS Warehouse, Medium/Bulky Items on Pallets | SS Warehouse, Medium/Bulky Items on Pallets | SS Warehouse Medium/Bulky Material Storage | SS Warehouse Medium/Bulky Material Storage | SS Warehouse Medium/Bulky Material Storage | Warehouse | Nonrefrigerated warehouse PBA | Unrefrigerated Warehouse | SS Warehouse Medium/Bulky material | SO Commercial and Industrial Storage (conditioned or unconditioned)
SS Warehouse, Smaller Hand Carried Items | SS Warehouse, Smaller Hand Carried Items | SS Warehouse Fine Material Storage | SS Warehouse Fine Material Storage | SS Warehouse Fine Material Storage | Warehouse | Nonrefrigerated warehouse PBA | Unrefrigerated Warehouse | SS Warehouse Fine material | SO Commercial and Industrial Storage (conditioned or unconditioned)
|  | Not assiogned | Not assigned | Not assigned
|  | CS Sales Area | CS Active Storage Hospital | SS Active Storage Hospital
|  |  | CS Audience/Seating Area Exercise Center | SS Audience/Seating Area Exercise Center
|  |  | CS Sales Area | SS Parking Garage Attendant Only
Note on G7: Charles Eley: Map to 50% government office and 50% public assembly
Note on A98: Charles Eley: This is not a common space type if it is specific to hospitals.

## 90.1-2016 PRM (hidden)
| Lookup Name | Allowed Lighting Power (W/ft²) | Occupant Sensor | Notes | Reference Material to Standard
Table G3.8 -- Lighting Power Densities Using the Building Area Method | BA Automotive Facility | 0.9 | n.a. |  | BA | Automotive Facility
| BA Convention Center | 1.2 | n.a. |  | BA | Convention Center
| BA Courthouse | 1.2 | n.a. |  | BA | Courthouse
| BA Dining: Bar Lounge/Leisure | 1.3 | n.a. |  | BA | Dining: Bar Lounge/Leisure
| BA Dining: Cafeteria/Fast Food | 1.4 | n.a. |  | BA | Dining: Cafeteria/Fast Food
| BA Dining: Family | 1.6 | n.a. |  | BA | Dining: Family
| BA Dormitory | 1 | n.a. |  | BA | Dormitory
| BA Exercise Center | 1 | n.a. |  | BA | Exercise Center
| BA Fire Station | 1 | n.a. |  | BA | Fire Station
| BA Gymnasium | 1.1 | n.a. |  | BA | Gymnasium
| BA Healthcare Clinic | 1 | n.a. |  | BA | Healthcare Clinic
| BA Hospital | 1.2 | n.a. |  | BA | Hospital
| BA Hotel/Motel | 1.09 | n.a. |  | BA | Hotel/Motel
| BA Library | 1.3 | n.a. |  | BA | Library
| BA Manufacturing Facility | 1.17 | n.a. |  | BA | Manufacturing Facility
| BA Motion Picture Theater | 1.2 | n.a. |  | BA | Motion Picture Theater
| BA Multifamily | 0.7 | n.a. |  | BA | Multifamily
| BA Museum | 1.1 | n.a. |  | BA | Museum
| BA Office | 1 | n.a. |  | BA | Office
| BA Parking Garage | 0.3 | n.a. |  | BA | Parking Garage
| BA Penitentiary | 1 | n.a. |  | BA | Penitentiary
| BA Performing Arts Theater | 1.6 | n.a. |  | BA | Performing Arts Theater
| BA Police Station | 1 | n.a. |  | BA | Police Station
| BA Post Office | 1.1 | n.a. |  | BA | Post Office
| BA Religious Building | 1.3 | n.a. |  | BA | Religious Building
| BA Retail | 1.5 | n.a. |  | BA | Retail
| BA School/University | 1.2 | n.a. |  | BA | School/University
| BA Sports Arena | 1.1 | n.a. |  | BA | Sports Arena
| BA Town Hall | 1.1 | n.a. |  | BA | Town Hall
| BA Transportation | 1 | n.a. |  | BA | Transportation
| BA Warehouse | 0.8 | n.a. |  | BA | Warehouse
| BA Workshop | 1.4 | n.a. |  | BA | Workshop
Table G3.7 Common Space Types | CS Audience Seating Area, Auditorium | 0.9 | 10% |  | CS | Audience Seating Area | Auditorium
| CS Audience Seating Area, Convention Center | 0.7 | 10% |  | CS | Audience Seating Area | Convention Center
| CS Audience Seating Area, Exercise Center | 0.3 | 10% |  | CS | Audience Seating Area | Exercise Center
| CS Audience Seating Area, Gymnasium | 0.4 | 10% |  | CS | Audience Seating Area | Gymnasium
| CS Audience Seating Area, Motion Picture Theater | 1.2 | 10% |  | CS | Audience Seating Area | Motion Picture Theater
| CS Audience Seating Area, Penitentiary | 0.7 | 10% |  | CS | Audience Seating Area | Penitentiary
| CS Audience Seating Area, Performing Arts Theater | 2.6 | 10% |  | CS | Audience Seating Area | Performing Arts Theater
| CS Audience Seating Area, Religious Building | 1.7 | 10% |  | CS | Audience Seating Area | Religious Building
| CS Audience Seating Area, Sports Arena | 0.4 | 10% |  | CS | Audience Seating Area | Sports Arena
| CS Audience Seating Area, Transportation Facility | 0.5 | 10% |  | CS | Audience Seating Area | Transportation Facility
| CS Audience Seating Area, Other | 0.9 | 10% |  | CS | Audience Seating Area | Other
| CS Atrium, Less than or equal to 40 ft | 0.0375 per ft of height | 10% |  | CS | Atrium | Less than or equal to 40 ft
| CS Atrium, More than 40 ft | 0.05 + 0.025 per ft of height | 10% |  | CS | Atrium | More than 40 ft
| CS Banking Activity Area, | 1.5 | 10% |  | CS | Banking Activity Area
| CS Classroom/Lecture/Training, Penitentiary | 1.3 | n.a. |  | CS | Classroom/Lecture/Training | Penitentiary
| CS Classroom/Lecture/Training, K-12, laboratory and shops | 1.4 | 30% |  | CS | Classroom/Lecture/Training | K-12, laboratory and shops
| CS Classroom/Lecture/Training, Other | 1.4 | n.a. |  | CS | Classroom/Lecture/Training | Other
| CS Conference/Meeting/Multipurpose, | 1.3 | n.a. |  | CS | Conference/Meeting/Multipurpose
| CS Confinment Cells, | 0.9 | 10% |  | CS | Confinment Cells
| CS Copy/Print Room, | 0.9 | 10% |  | CS | Copy/Print Room
| CS Corridor, Assisted Living | 1.15 | 25% |  | CS | Corridor | Assisted Living
| CS Corridor, Hospital | 1 | 25% |  | CS | Corridor | Hospital
| CS Corridor, Manufacturing | 0.5 | 25% |  | CS | Corridor | Manufacturing
| CS Corridor, Other | 0.5 | 25% |  | CS | Corridor | Other
| CS Courtroom, | 1.9 | 10% |  | CS | Courtroom
| CS Computer Room, | 2.14 | 35% |  | CS | Computer Room
| CS Dining Area, Penitentiary | 1.3 | 35% |  | CS | Dining Area | Penitentiary
| CS Dining Area, Assisted Living | 3.32 | 35% |  | CS | Dining Area | Assisted Living
| CS Dining Area, Bar Lounge/Leisure | 1.4 | 35% |  | CS | Dining Area | Bar Lounge/Leisure
| CS Dining Area, Cafeteria or Fast Food | 0.9 | 35% |  | CS | Dining Area | Cafeteria or Fast Food
| CS Dining Area, Family Dining | 2.1 | 35% |  | CS | Dining Area | Family Dining
| CS Dining Area, Other | 0.9 | 35% |  | CS | Dining Area | Other
| CS Electrical/Mechanical , | 1.5 | 30% |  | CS | Electrical/Mechanical
| CS Emergency Vehicle Garage, | 0.8 | 10% |  | CS | Emergency Vehicle Garage
| CS Food Preparation , | 1.2 | 30% |  | CS | Food Preparation
| CS Guest Room, | 1.1 | 45% |  | CS | Guest Room
| CS Judges Chambers, | 1.3 | 30% |  | CS | Judges Chambers
| CS Laboratory, Classrooms | 1.4 | None |  | CS | Laboratory | Classrooms
| CS Laboratory, Other | 1.4 | 10% |  | CS | Laboratory | Other
| CS Laundry/Washing Area, | 0.6 | 10% |  | CS | Laundry/Washing Area
| CS Loading Dock, Interior, | 0.59 | 10% |  | CS | Loading Dock, Interior
| CS Lobby, Assisted Living | 2.26 | 25% |  | CS | Lobby | Assisted Living
| CS Lobby, Elevator | 0.8 | 25% |  | CS | Lobby | Elevator
| CS Lobby, Hotel | 1.1 | 25% |  | CS | Lobby | Hotel
| CS Lobby, Motion Picture Theater | 1.1 | 25% |  | CS | Lobby | Motion Picture Theater
| CS Lobby, Performing Arts Theater | 3.3 | 25% |  | CS | Lobby | Performing Arts Theater
| CS Lobby, Other | 1.3 | 25% |  | CS | Lobby | Other
| CS Locker Room , | 0.6 | 25% |  | CS | Locker Room
| CS Lounge/Break, Healthcare | 0.8 | n.a. |  | CS | Lounge/Break | Healthcare
| CS Lounge/Break, Other | 1.2 | n.a. |  | CS | Lounge/Break | Other
| CS Office, Enclosed | 1.1 | 30% |  | CS | Office | Enclosed
| CS Office, Open Plan | 1.1 | 15% |  | CS | Office | Open Plan
| CS Parking Area, Interior, | 0.2 | 15% |  | CS | Parking Area, Interior
| CS Pharmacy Area, | 1.2 | 10% |  | CS | Pharmacy Area
| CS Restrooms , Assisted Living | 1.52 | 45% |  | CS | Restrooms | Assisted Living
| CS Restrooms , Other | 0.9 | 45% |  | CS | Restrooms | Other
| CS Sales Area, | 1.7 | 10% |  | CS | Sales Area
| CS Seating Area General, | 0.68 | 10% |  | CS | Seating Area General
| CS Stairway, | 0.6 | 75% |  | CS | Stairway
| CS Storage, Hospital | 0.9 | 45% |  | CS | Storage | Hospital
| CS Storage, >= 50 ft² | 0.8 | 45% |  | CS | Storage | >= 50 ft²
| CS Storage, < 50 ft² | 0.8 | 45% |  | CS | Storage | < 50 ft²
| CS Vehicular Maintenance, | 0.7 | 10% |  | CS | Vehicular Maintenance
| CS Workshop, | 1.9 | 10% |  | CS | Workshop
Table G3.7 -- Space-by-Space Lighting Power and PAFs | SS Assisted Living, Chapel | 2.77 | 10% |  | SS | Assisted Living | Chapel
| SS Assisted Living, Recreation Room | 3.02 | 10% |  | SS | Assisted Living | Recreation Room
| SS Convention Center, Exhibit Space | 1.3 | 35% |  | SS | Convention Center | Exhibit Space
| SS Dormitory, Living Quarters | 1.11 | 10% |  | SS | Dormitory | Living Quarters
| SS Fire Station, Sleeping Quarters | 0.3 | 10% |  | SS | Fire Station | Sleeping Quarters
| SS Gymnasium/Fitness Center, Exercise Area | 0.9 | 35% |  | SS | Gymnasium/Fitness Center | Exercise Area
| SS Gymnasium/Fitness Center, Playing Area | 1.4 | 35% |  | SS | Gymnasium/Fitness Center | Playing Area
| SS Healthcare, Emergency Room | 2.7 | 10% |  | SS | Healthcare | Emergency Room
| SS Healthcare, Exam/Treatment | 1.5 | 10% |  | SS | Healthcare | Exam/Treatment
| SS Healthcare, Supply Room | 1.4 | 45% |  | SS | Healthcare | Supply Room
| SS Healthcare, Nursery | 0.6 | 10% |  | SS | Healthcare | Nursery
| SS Healthcare, Nurses’ Station | 1 | 10% |  | SS | Healthcare | Nurses’ Station
| SS Healthcare, Operating Room | 2.2 | 10% |  | SS | Healthcare | Operating Room
| SS Healthcare, Patient Room | 0.7 | 10% |  | SS | Healthcare | Patient Room
| SS Healthcare, Physical Therapy | 0.9 | 10% |  | SS | Healthcare | Physical Therapy
| SS Healthcare, Recovery Room | 0.8 | 10% |  | SS | Healthcare | Recovery Room
| SS Library, Reading Area | 1.2 | 15% |  | SS | Library | Reading Area
| SS Library, Stacks | 1.7 | 15% |  | SS | Library | Stacks
| SS Manufacturing Facility, Detailed Manufacturing | 2.1 | 10% |  | SS | Manufacturing Facility | Detailed Manufacturing
| SS Manufacturing Facility, Equipment Room | 1.2 | 10% |  | SS | Manufacturing Facility | Equipment Room
| SS Manufacturing Facility, Extra High Bay (>50 ft Floor to Ceiling Height) | 1.32 | 10% |  | SS | Manufacturing Facility | Extra High Bay (>50 ft Floor to Ceiling Height)
| SS Manufacturing Facility, High Bay (25–50 ft Floor to Ceiling Height) | 1.7 | 10% |  | SS | Manufacturing Facility | High Bay (25–50 ft Floor to Ceiling Height)
| SS Manufacturing Facility, Low Bay (<25 ft Floor to Ceiling Height) | 1.2 | 10% |  | SS | Manufacturing Facility | Low Bay (<25 ft Floor to Ceiling Height)
| SS Museum, General Exhibition | 1 | 10% |  | SS | Museum | General Exhibition
| SS Museum, Restoration | 1.7 | 10% |  | SS | Museum | Restoration
| SS Post Office, Sorting Area | 1.2 | 10% |  | SS | Post Office | Sorting Area
| SS Religious Building, Fellowship Hall | 0.9 | 10% |  | SS | Religious Building | Fellowship Hall
| SS Religious Building, Worship/Pulpit/Choir | 2.4 | 10% |  | SS | Religious Building | Worship/Pulpit/Choir
| SS Retail, Dressing/Fitting Room | 0.89 | 10% |  | SS | Retail | Dressing/Fitting Room
| SS Retail, Mall Concourse | 1.7 | 10% |  | SS | Retail | Mall Concourse
| SS Sports Arena Playing Area, Class I | 4.61 | 10% |  | SS | Sports Arena Playing Area | Class I
| SS Sports Arena Playing Area, Class II | 3.01 | 10% |  | SS | Sports Arena Playing Area | Class II
| SS Sports Arena Playing Area, Class III | 2.26 | 10% |  | SS | Sports Arena Playing Area | Class III
| SS Sports Arena Playing Area, Class IV | 1.5 | 10% |  | SS | Sports Arena Playing Area | Class IV
| SS Transportation, Baggage/Carousel Area | 1 | 10% |  | SS | Transportation | Baggage/Carousel Area
| SS Transportation, Concourse | 0.6 | 10% |  | SS | Transportation | Concourse
| SS Transportation, Ticket Counter | 1.5 | 10% |  | SS | Transportation | Ticket Counter
| SS Warehouse, Medium/Bulky Items on Pallets | 0.9 | 15% |  | SS | Warehouse | Medium/Bulky Items on Pallets
| SS Warehouse, Smaller Hand Carried Items | 1.4 | 15% |  | SS | Warehouse | Smaller Hand Carried Items
[7 empty] | Stairway | 0.69 | 10
[7 empty] | Storage, Inactive, General | 0.63 | 6

## 90.1-2010 (hidden)
| Lookup Name | W/ft² | RCR Threshold | Notes | Reference Material to Standard
TABLE 9.5.1 Lighting Power Densities Using the Building Area Method | BA Automotive Facility | 0.82 | n.a. |  | BA | Automotive Facility
| BA Convention Center | 1.08 | n.a. |  | BA | Convention Center
| BA Courthouse | 1.05 | n.a. |  | BA | Courthouse
| BA Dining: Bar Lounge/Leisure | 0.99 | n.a. |  | BA | Dining: Bar Lounge/Leisure
| BA Dining: Cafeteria/Fast Food | 0.9 | n.a. |  | BA | Dining: Cafeteria/Fast Food
| BA Dining: Family | 0.89 | n.a. |  | BA | Dining: Family
| BA Dormitory | 0.61 | n.a. |  | BA | Dormitory
| BA Exercise Center | 0.88 | n.a. |  | BA | Exercise Center
| BA Fire Station | 0.71 | n.a. |  | BA | Fire Station
| BA Gymnasium | 1 | n.a. |  | BA | Gymnasium
| BA Healthcare Clinic | 0.87 | n.a. |  | BA | Healthcare Clinic
| BA Hospital | 1.21 | n.a. |  | BA | Hospital
| BA Hotel | 1 | n.a. |  | BA | Hotel
| BA Library | 1.18 | n.a. |  | BA | Library
| BA Manufacturing Facility | 1.11 | n.a. |  | BA | Manufacturing Facility
| BA Motel | 0.88 | n.a. |  | BA | Motel
| BA Motion Picture Theater | 0.83 | n.a. |  | BA | Motion Picture Theater
| BA Multifamily | 0.6 | n.a. |  | BA | Multifamily
| BA Museum | 1.06 | n.a. |  | BA | Museum
| BA Office | 0.9 | n.a. |  | BA | Office
| BA Parking Garage | 0.25 | n.a. |  | BA | Parking Garage
| BA Penitentiary | 0.97 | n.a. |  | BA | Penitentiary
| BA Performing Arts Theater | 1.36 | n.a. |  | BA | Performing Arts Theater
| BA Police Station | 0.96 | n.a. |  | BA | Police Station
| BA Post Office | 0.87 | n.a. |  | BA | Post Office
| BA Religious Building | 1.05 | n.a. |  | BA | Religious Building
| BA Retail | 1.4 | n.a. |  | BA | Retail
| BA School/University | 0.99 | n.a. |  | BA | School/University
| BA Sports Arena | 0.78 | n.a. |  | BA | Sports Arena
| BA Town Hall | 0.92 | n.a. |  | BA | Town Hall
| BA Transportation | 0.77 | n.a. |  | BA | Transportation
| BA Warehouse | 0.66 | n.a. |  | BA | Warehouse
| BA Workshop | 1.2 | n.a. |  | BA | Workshop
Common Space Types | CS Atrium First 40 ft in Height | 0.03 (watts per ft height) | n.a. |  | CS | Atrium | First 40 ft in Height
| CS Atrium Height Above 40 ft | 0.02 (watts per ft height) | n.a. |  | CS | Atrium | Height Above 40 ft
| CS Audience Seating Permanent Auditorium | 0.79 | 6 |  | CS | Audience Seating Permanent | Auditorium
| CS Audience Seating Permanent Motion Picture Theater | 2.43 | 8 |  | CS | Audience Seating Permanent | Motion Picture Theater
| CS Audience Seating Permanent Performing Arts Theater | 1.14 | 4 |  | CS | Audience Seating Permanent | Performing Arts Theater
| CS Classroom/Lecture/Training | 1.24 | 4 |  | CS | Classroom/Lecture/Training
| CS Conference/Meeting/Multipurpose | 1.23 | 6 |  | CS | Conference/Meeting/Multipurpose
| CS Corridor/Transition | 0.66 | Width<8 ft |  | CS | Corridor/Transition
| CS Dining Area General | 0.65 | 4 |  | CS | Dining Area | General
| CS Dining Area Bar Lounge/Leisure Dining | 1.31 | 4 |  | CS | Dining Area | Bar Lounge/Leisure Dining
| CS Dining Area Family Dining | 0.89 | 4 |  | CS | Dining Area | Family Dining
| CS Dressing/Fitting Room Performing Arts Theater | 0.4 | 6 |  | CS | Dressing/Fitting Room Performing Arts Theater
| CS Electrical/Mechanical | 0.95 | 6 |  | CS | Electrical/Mechanical
| CS Food Preparation | 0.99 | 6 |  | CS | Food Preparation
| CS Laboratory Classrooms | 1.28 | 6 |  | CS | Laboratory | Classrooms
| CS Laboratory Medical/Industrial/Research | 1.81 | 6 |  | CS | Laboratory | Medical/Industrial/Research
| CS Lobby General | 0.9 | 4 |  | CS | Lobby | General
| CS Lobby Elevator | 0.64 | 6 |  | CS | Lobby | Elevator
| CS Lobby Motion Picture Theater | 2 | 6 |  | CS | Lobby | Motion Picture Theater
| CS Lobby Performing Arts Theater | 0.52 | 4 |  | CS | Lobby | Performing Arts Theater
| CS Locker Room | 0.75 | 6 |  | CS | Locker Room
| CS Lounge/Recreation | 0.73 | 4 |  | CS | Lounge/Recreation
| CS Office Enclosed | 1.11 | 8 |  | CS | Office | Enclosed
| CS Office Open Plan | 0.98 | 4 |  | CS | Office | Open Plan
| CS Restrooms | 0.98 | 8 |  | CS | Restrooms
| CS Sales Area | 1.68 | 6 |  | CS | Sales Area
| CS Stairway | 0.69 | 10 |  | CS | Stairway
| CS Storage | 0.63 | 6 |  | CS | Storage
| CS Workshop, General | 1.59 | 6 |  | CS | Workshop, General
Building-Specific Space Types | SS Automotive Service/Repair | 0.67 | 4 |  | SS | Automotive | Service/Repair
| SS Bank/Office Banking Activity Area | 1.38 | 6 |  | SS | Bank/Office | Banking Activity Area
| SS Convention Center Audience Seating | 0.82 | 4 |  | SS | Convention Center | Audience Seating
| SS Convention Center Exhibit Space | 1.45 | 4 |  | SS | Convention Center | Exhibit Space
| SS Courthouse/Police Station/Penitentiary Courtroom | 1.72 | 6 |  | SS | Courthouse/Police Station/Penitentiary | Courtroom
| SS Courthouse/Police Station/Penitentiary Confinement Cells | 1.1 | 6 |  | SS | Courthouse/Police Station/Penitentiary | Confinement Cells
| SS Courthouse/Police Station/Penitentiary Judges’ Chambers | 1.17 | 8 |  | SS | Courthouse/Police Station/Penitentiary | Judges’ Chambers
| SS Courthouse/Police Station/Penitentiary Penitentiary Audience Seating | 0.43 | 4 |  | SS | Courthouse/Police Station/Penitentiary | Penitentiary Audience Seating
| SS Courthouse/Police Station/Penitentiary Penitentiary Classroom | 1.34 | 4 |  | SS | Courthouse/Police Station/Penitentiary | Penitentiary Classroom
| SS Courthouse/Police Station/Penitentiary Penitentiary Dining | 1.07 | 6 |  | SS | Courthouse/Police Station/Penitentiary | Penitentiary Dining
| SS Dormitory Living Quarters | 0.38 | 8 |  | SS | Dormitory | Living Quarters
| SS Fire Stations Engine Room | 0.56 | 4 |  | SS | Fire Stations | Engine Room
| SS Fire Stations Sleeping Quarters | 0.25 | 6 |  | SS | Fire Stations | Sleeping Quarters
| SS Gymnasium/Fitness Center Fitness Area | 0.72 | 4 |  | SS | Gymnasium/Fitness Center | Fitness Area
| SS Gymnasium/Fitness Center Gymnasium Audience Seating | 0.43 | 6 |  | SS | Gymnasium/Fitness Center | Gymnasium Audience Seating
| SS Gymnasium/Fitness Center Playing Area | 1.2 | 4 |  | SS | Gymnasium/Fitness Center | Playing Area
| SS Hospital Corridor/Transition | 0.89 | Width < 8 ft |  | SS | Hospital | Corridor/Transition
| SS Hospital Emergency | 2.26 | 6 |  | SS | Hospital | Emergency
| SS Hospital Exam/Treatment | 1.66 | 8 |  | SS | Hospital | Exam/Treatment
| SS Hospital Laundry/Washing | 0.6 | 4 |  | SS | Hospital | Laundry/Washing
| SS Hospital Lounge/Recreation | 1.07 | 6 |  | SS | Hospital | Lounge/Recreation
| SS Hospital Medical Supply | 1.27 | 6 |  | SS | Hospital | Medical Supply
| SS Hospital Nursery | 0.88 | 6 |  | SS | Hospital | Nursery
| SS Hospital Nurses’ Station | 0.87 | 6 |  | SS | Hospital | Nurses’ Station
| SS Hospital Operating Room | 1.89 | 6 |  | SS | Hospital | Operating Room
| SS Hospital Patient Room | 0.62 | 6 |  | SS | Hospital | Patient Room
| SS Hospital Pharmacy | 1.14 | 6 |  | SS | Hospital | Pharmacy
| SS Hospital Physical Therapy | 0.91 | 6 |  | SS | Hospital | Physical Therapy
| SS Hospital Radiology/Imaging | 1.32 | 6 |  | SS | Hospital | Radiology/Imaging
| SS Hospital Recovery | 1.15 | 6 |  | SS | Hospital | Recovery
| SS Hotel/Highway Lodging Hotel Dining | 0.82 | 4 |  | SS | Hotel/Highway Lodging | Hotel Dining
| SS Hotel/Highway Lodging Hotel Guest Rooms | 1.11 | 6 |  | SS | Hotel/Highway Lodging | Hotel Guest Rooms
| SS Hotel/Highway Lodging Hotel Lobby | 1.06 | 4 |  | SS | Hotel/Highway Lodging | Hotel Lobby
| SS Hotel/Highway Lodging Highway Lodging Dining | 0.88 | 4 |  | SS | Hotel/Highway Lodging | Highway Lodging Dining
| SS Hotel/Highway Lodging Highway Lodging Guest Rooms | 0.75 | 6 |  | SS | Hotel/Highway Lodging | Highway Lodging Guest Rooms
| SS Library Card File and Cataloging | 0.72 | 4 |  | SS | Library | Card File and Cataloging
| SS Library Reading Area | 0.93 | 4 |  | SS | Library | Reading Area
| SS Library Stacks | 1.71 | 4 |  | SS | Library | Stacks
| SS Manufacturing Corridor/Transition | 0.41 | Width < 8 ft |  | SS | Manufacturing | Corridor/Transition
| SS Manufacturing Detailed Manufacturing | 1.29 | 4 |  | SS | Manufacturing | Detailed Manufacturing
| SS Manufacturing Equipment Room | 0.95 | 6 |  | SS | Manufacturing | Equipment Room
| SS Manufacturing Extra High Bay (>50 ft Floor to Ceiling Height) | 1.05 | 4 |  | SS | Manufacturing | Extra High Bay (>50 ft Floor to Ceiling Height)
| SS Manufacturing High Bay (25–50 ft Floor to Ceiling Height) | 1.23 | 4 |  | SS | Manufacturing | High Bay (25–50 ft Floor to Ceiling Height)
| SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height) | 1.19 | 4 |  | SS | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height)
| SS Museum General Exhibition | 1.05 | 6 |  | SS | Museum | General Exhibition
| SS Museum Restoration | 1.02 | 6 |  | SS | Museum | Restoration
| SS Parking Garage Garage Area | 0.19 | 4 |  | SS | Parking Garage | Garage Area
| SS Post Office Sorting Area | 0.94 | 4 |  | SS | Post Office | Sorting Area
| SS Religious Buildings Audience Seating | 1.53 | 4 |  | SS | Religious Buildings | Audience Seating
| SS Religious Buildings Fellowship Hall | 0.64 | 4 |  | SS | Religious Buildings | Fellowship Hall
| SS Religious Buildings Worship Pulpit, Choir | 1.53 | 4 |  | SS | Religious Buildings | Worship Pulpit, Choir
| SS Retail Dressing/Fitting Room | 0.87 | 8 |  | SS | Retail | Dressing/Fitting Room
| SS Retail Mall Concourse | 1.1 | 4 |  | SS | Retail | Mall Concourse
| SS Retail Sales Area | 1.68 | 6 |  | SS | Retail | Sales Area
| SS Sports Arena Audience Seating | 0.43 | 4 |  | SS | Sports Arena | Audience Seating
| SS Sports Arena Court Sports Arena—Class 1 | 0.72 | 4 |  | SS | Sports Arena | Court Sports Arena—Class 1
| SS Sports Arena Court Sports Arena—Class 2 | 1.2 | 4 |  | SS | Sports Arena | Court Sports Arena—Class 2
| SS Sports Arena Court Sports Arena—Class 3 | 1.92 | 4 |  | SS | Sports Arena | Court Sports Arena—Class 3
| SS Sports Arena Court Sports Arena—Class 4 | 3.01 | 4 |  | SS | Sports Arena | Court Sports Arena—Class 4
| SS Sports Arena Indoor Sports Fields | 0.72 | 4 |  | SS | Sports Arena | Indoor Sports Fields
| SS Sports Arena Ring Sports Arena | 2.68 | 4 |  | SS | Sports Arena | Ring Sports Arena
| SS Transportation Air/Train/Bus—Baggage Area | 0.76 | 4 |  | SS | Transportation | Air/Train/Bus—Baggage Area
| SS Transportation Airport—Concourse | 0.36 | 4 |  | SS | Transportation | Airport—Concourse
| SS Transportation Audience Seating | 0.54 | 4 |  | SS | Transportation | Audience Seating
| SS Transportation Terminal—Ticket Counter | 1.08 | 4 |  | SS | Transportation | Terminal—Ticket Counter
| SS Warehouse Fine Material Storage | 0.95 | 6 |  | SS | Warehouse | Fine Material Storage
| SS Warehouse Medium/Bulky Material Storage | 0.58 | 4 |  | SS | Warehouse | Medium/Bulky Material Storage
Extras
| Equipment Room | 0.95 | 6
| Home Nursing/Senior Housing | 1.11 | 6
| Laundry Facility | 0.6 | 4
| Mechanical Control Room | 0.95 | 6
| Storage, Active, Musuem | 0.63 | 6
| Storage, Inactive, Musuem | 0.63 | 6
| Warehouse, Refrigerated | 0.58 | 4
[7 empty] | Stairway | 0.69 | 10
[7 empty] | Storage, Inactive, General | 0.63 | 6

## 90.1-2007 (hidden)
| Lookup Name | W/ft² | Notes | Reference Material to Standard
TABLE 9.5.1 Lighting Power Densities Using the Building Area Method | BA Automotive facility | 0.9 |  | BA | Automotive facility
| BA Convention center | 1.2 |  | BA | Convention center
| BA Courthouse | 1.2 |  | BA | Courthouse
| BA Dining: bar lounge/leisure | 1.3 |  | BA | Dining: bar lounge/leisure
| BA Dining: cafeteria/fast food | 1.4 |  | BA | Dining: cafeteria/fast food
| BA Dining: family | 1.6 |  | BA | Dining: family
| BA Dormitory | 1 |  | BA | Dormitory
| BA Exercise center | 1 |  | BA | Exercise center
| BA Gymnasium | 1.1 |  | BA | Gymnasium
| BA Health-care clinic | 1 |  | BA | Health-care clinic
| BA Hospital | 1.2 |  | BA | Hospital
| BA Hotel | 1 |  | BA | Hotel
| BA Library | 1.3 |  | BA | Library
| BA Manufacturing facility | 1.3 |  | BA | Manufacturing facility
| BA Motel | 1 |  | BA | Motel
| BA Motion picture theater | 1.2 |  | BA | Motion picture theater
| BA Multifamily | 0.7 |  | BA | Multifamily
| BA Museum | 1.1 |  | BA | Museum
| BA Office | 1 |  | BA | Office
| BA Parking garage | 0.3 |  | BA | Parking garage
| BA Penitentiary | 1 |  | BA | Penitentiary
| BA Performing arts theater | 1.6 |  | BA | Performing arts theater
| BA Police/fire station | 1 |  | BA | Police/fire station
| BA Post office | 1.1 |  | BA | Post office
| BA Religious building | 1.3 |  | BA | Religious building
| BA Retail | 1.5 |  | BA | Retail
| BA School/university | 1.2 |  | BA | School/university
| BA Sports arena | 1.1 |  | BA | Sports arena
| BA Town hall | 1.1 |  | BA | Town hall
| BA Transportation | 1 |  | BA | Transportation
| BA Warehouse | 0.8 |  | BA | Warehouse
| BA Workshop | 1.4 |  | BA | Workshop
Common Space Types | CS Office Enclosed | 1.1 |  | CS | Office | Enclosed
| CS Office Open Plan | 1.1 |  | CS | Office | Open Plan
| CS Conference/Meeting/Multipurpose | 1.3 |  | CS | Conference/Meeting/Multipurpose
| CS Classroom/Lecture/Training General | 1.4 |  | CS | Classroom/Lecture/Training | General
| CS Classroom/Lecture/Training Penitentiary | 1.3 |  | CS | Classroom/Lecture/Training | Penitentiary
| CS Lobby General | 1.3 |  | CS | Lobby | General
| CS Lobby Hotel | 1.1 |  | CS | Lobby | Hotel
| CS Lobby Performing Arts Theater | 3.3 |  | CS | Lobby | Performing Arts Theater
| CS Lobby Motion Picture Theater | 1.1 |  | CS | Lobby | Motion Picture Theater
| CS Audience/Seating Area General | 0.9 |  | CS | Audience/Seating Area | General
| CS Audience/Seating Area Gymnasium | 0.4 |  | CS | Audience/Seating Area | Gymnasium
| CS Audience/Seating Area Exercise Center | 0.3 |  | CS | Audience/Seating Area | Exercise Center
| CS Audience/Seating Area Convention Center | 0.7 |  | CS | Audience/Seating Area | Convention Center
| CS Audience/Seating Area Penitentiary | 0.7 |  | CS | Audience/Seating Area | Penitentiary
| CS Audience/Seating Area Religious Buildings | 1.7 |  | CS | Audience/Seating Area | Religious Buildings
| CS Audience/Seating Area Sports Arena | 0.4 |  | CS | Audience/Seating Area | Sports Arena
| CS Audience/Seating Area Performing Arts Theater | 2.6 |  | CS | Audience/Seating Area | Performing Arts Theater
| CS Audience/Seating Area Motion Picture Theater | 1.2 |  | CS | Audience/Seating Area | Motion Picture Theater
| CS Audience/Seating Area Transportation | 0.5 |  | CS | Audience/Seating Area | Transportation
| CS Atrium—First Three Floors | 0.6 |  | CS | Atrium—First Three Floors
| CS Atrium—Each Additional Floor | 0.2 |  | CS | Atrium—Each Additional Floor
| CS Lounge/Recreation General | 1.2 |  | CS | Lounge/Recreation | General
| CS Lounge/Recreation Hospital | 0.8 |  | CS | Lounge/Recreation | Hospital
| CS Dining Area General | 0.9 |  | CS | Dining Area | General
| CS Dining Area Penitentiary | 1.3 |  | CS | Dining Area | Penitentiary
| CS Dining Area Hotel | 1.3 |  | CS | Dining Area | Hotel
| CS Dining Area Motel | 1.2 |  | CS | Dining Area | Motel
| CS Dining Area Bar Lounge/Leisure Dining | 1.4 |  | CS | Dining Area | Bar Lounge/Leisure Dining
| CS Dining Area Family Dining | 2.1 |  | CS | Dining Area | Family Dining
| CS Food Preparation | 1.2 |  | CS | Food Preparation
| CS Laboratory | 1.4 |  | CS | Laboratory
| CS Restrooms | 0.9 |  | CS | Restrooms
| CS Dressing/Locker/Fitting Room | 0.6 |  | CS | Dressing/Locker/Fitting Room
| CS Corridor/Transition General | 0.5 |  | CS | Corridor/Transition | General
| CS Corridor/Transition Hospital | 1 |  | CS | Corridor/Transition | Hospital
| CS Corridor/Transition Manufacturing Facility | 0.5 |  | CS | Corridor/Transition | Manufacturing Facility
| CS Stairs—Active | 0.6 |  | CS | Stairs—Active
| CS Active Storage General | 0.8 |  | CS | Active Storage | General
| CS Active Storage Hospital | 0.9 |  | CS | Active Storage | Hospital
| CS Inactive Storage General | 0.3 |  | CS | Inactive Storage | General
| CS Inactive Storage Museum | 0.8 |  | CS | Inactive Storage | Museum
| CS Electrical/Mechanical | 1.5 |  | CS | Electrical/Mechanical
| CS Workshop | 1.9 |  | CS | Workshop
| CS Sales Area | 1.7 | For accent lighting, see Section 9.6.2(b) | CS | Sales Area
Specific Space Types | SS Gymnasium/Exercise Center Playing Area | 1.4 |  | SS | Gymnasium/Exercise Center | Playing Area
| SS Gymnasium/Exercise Center Exercise Area | 0.9 |  | SS | Gymnasium/Exercise Center | Exercise Area
| SS Courthouse/Police Station/Penitentiary Courtroom | 1.9 |  | SS | Courthouse/Police Station/Penitentiary | Courtroom
| SS Courthouse/Police Station/Penitentiary Confinement Cells | 0.9 |  | SS | Courthouse/Police Station/Penitentiary | Confinement Cells
| SS Courthouse/Police Station/Penitentiary Judges’ Chambers | 1.3 |  | SS | Courthouse/Police Station/Penitentiary | Judges’ Chambers
| SS Fire Stations Engine Room | 0.8 |  | SS | Fire Stations | Engine Room
| SS Fire Stations Sleeping Quarters | 0.3 |  | SS | Fire Stations | Sleeping Quarters
| SS Post Office—Sorting Area | 1.2 |  | SS | Post Office—Sorting Area
| SS Convention Center Exhibit Space | 1.3 |  | SS | Convention Center | Exhibit Space
| SS Library Card File and Cataloging | 1.1 |  | SS | Library | Card File and Cataloging
| SS Library Stacks | 1.7 |  | SS | Library | Stacks
| SS Library Reading Area | 1.2 |  | SS | Library | Reading Area
| SS Hospital Emergency | 2.7 |  | SS | Hospital | Emergency
| SS Hospital Recovery | 0.8 |  | SS | Hospital | Recovery
| SS Hospital Nurses’ Station | 1 |  | SS | Hospital | Nurses’ Station
| SS Hospital Exam/Treatment | 1.5 |  | SS | Hospital | Exam/Treatment
| SS Hospital Pharmacy | 1.2 |  | SS | Hospital | Pharmacy
| SS Hospital Patient Room | 0.7 |  | SS | Hospital | Patient Room
| SS Hospital Operating Room | 2.2 |  | SS | Hospital | Operating Room
| SS Hospital Nursery | 0.6 |  | SS | Hospital | Nursery
| SS Hospital Medical Supply | 1.4 |  | SS | Hospital | Medical Supply
| SS Hospital Physical Therapy | 0.9 |  | SS | Hospital | Physical Therapy
| SS Hospital Radiology | 0.4 |  | SS | Hospital | Radiology
| SS Hospital Laundry—Washing | 0.6 |  | SS | Hospital | Laundry—Washing
| SS Automotive Service Repair | 0.7 |  | SS | Automotive | Service Repair
| SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | SS | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height)
| SS Manufacturing High Bay (³25 ft Floor to Ceiling Height) | 1.7 |  | SS | Manufacturing | High Bay (³25 ft Floor to Ceiling Height)
| SS Manufacturing Detailed Manufacturing | 2.1 |  | SS | Manufacturing | Detailed Manufacturing
| SS Manufacturing Equipment Room | 1.2 |  | SS | Manufacturing | Equipment Room
| SS Manufacturing Control Room | 0.5 |  | SS | Manufacturing | Control Room
| SS Hotel/Motel Guest Rooms | 1.1 |  | SS | Hotel/Motel | Guest Rooms
| SS Dormitory Living Quarters | 1.1 |  | SS | Dormitory | Living Quarters
| SS Museum General Exhibition | 1 |  | SS | Museum | General Exhibition
| SS Museum Restoration | 1.7 |  | SS | Museum | Restoration
| SS Bank/Office Banking Activity Area | 1.5 |  | SS | Bank/Office | Banking Activity Area
| SS Religious Buildings Worship Pulpit, Choir | 2.4 |  | SS | Religious Buildings | Worship Pulpit, Choir
| SS Religious Buildings Fellowship Hall | 0.9 |  | SS | Religious Buildings | Fellowship Hall
| SS Retail Sales Area | 1.7 | For accent lighting, see Section 9.6.3(c) | SS | Retail | Sales Area
| SS Retail Mall Concourse | 1.7 |  | SS | Retail | Mall Concourse
| SS Sports Arena Ring Sports Area | 2.7 |  | SS | Sports Arena | Ring Sports Area
| SS Sports Arena Court Sports Area | 2.3 |  | SS | Sports Arena | Court Sports Area
| SS Sports Arena Indoor Playing Field Area | 1.4 |  | SS | Sports Arena | Indoor Playing Field Area
| SS Warehouse Fine Material Storage | 1.4 |  | SS | Warehouse | Fine Material Storage
| SS Warehouse Medium/Bulky Material Storage | 0.9 |  | SS | Warehouse | Medium/Bulky Material Storage
| SS Parking Garage Garage Area | 0.2 |  | SS | Parking Garage | Garage Area
| SS Transportation Airport—Concourse | 0.6 |  | SS | Transportation | Airport—Concourse
| SS Transportation Air/Train/Bus—Baggage Area | 1 |  | SS | Transportation | Air/Train/Bus—Baggage Area
| SS Transportation Terminal—Ticket Counter | 1.5 |  | SS | Transportation | Terminal—Ticket Counter

## 90.1-2001 (hidden)
| Lookup Name | W/ft² | Notes | Reference Material to Standard
Building Type (Table 9.3.1.1) | BA Automotive Facility | 1.5 |  | BA | Automotive Facility
| BA Convention Center | 1.4 |  | BA | Convention Center
| BA Court House | 1.4 |  | BA | Court House
| BA Dining: Bar Lounge/Leisure | 1.5 |  | BA | Dining: Bar Lounge/Leisure
| BA Dining: Cafeteria/Fast Food | 1.8 |  | BA | Dining: Cafeteria/Fast Food
| BA Dining: Family | 1.9 |  | BA | Dining: Family
| BA Dormitory | 1.5 |  | BA | Dormitory
| BA Exercise Center | 1.4 |  | BA | Exercise Center
| BA Gymnasium | 1.7 |  | BA | Gymnasium
| BA Hospital/Health Care | 1.6 |  | BA | Hospital/Health Care
| BA Hotel | 1.7 |  | BA | Hotel
| BA Library | 1.5 |  | BA | Library
| BA Manufacturing Facility | 2.2 |  | BA | Manufacturing Facility
| BA Motel | 2 |  | BA | Motel
| BA Motion Picture Theater | 1.6 |  | BA | Motion Picture Theater
| BA Multi-Family | 1 |  | BA | Multi-Family
| BA Museum | 1.6 |  | BA | Museum
| BA Office | 1.3 |  | BA | Office
| BA Parking Garage | 0.3 |  | BA | Parking Garage
| BA Penitentiary | 1.2 |  | BA | Penitentiary
| BA Performing Arts Theater | 1.5 |  | BA | Performing Arts Theater
| BA Police/Fire Station | 1.3 |  | BA | Police/Fire Station
| BA Post Office | 1.6 |  | BA | Post Office
| BA Religious Building | 2.2 |  | BA | Religious Building
| BA Retail | 1.9 |  | BA | Retail
| BA School/University | 1.5 |  | BA | School/University
| BA Sports Arena | 1.5 |  | BA | Sports Arena
| BA Town Hall | 1.4 |  | BA | Town Hall
| BA Transportation | 1.2 |  | BA | Transportation
| BA Warehouse | 1.2 |  | BA | Warehouse
| BA Workshop | 1.7 |  | BA | Workshop
Common Space Types (Table 9.3.1.2) | CS Active Storage General | 1.1 |  | CS | Active Storage | General
| CS Atrium—Each Additional Floor | 0.2 |  | CS | Atrium—Each Additional Floor
| CS Atrium—First Three Floors | 1.3 |  | CS | Atrium—First Three Floors
| CS Audience/Seating Area General | 1.6 |  | CS | Audience/Seating Area | General
| CS Classroom/Lecture/Training General | 1.6 |  | CS | Classroom/Lecture/Training | General
| CS Conference/Meeting/Multipurpose | 1.5 |  | CS | Conference/Meeting/Multipurpose
| CS Stairs—Active | 0.9 |  | CS | Stairs—Active
| CS Corridor/Transition General | 0.7 |  | CS | Corridor/Transition | General
| CS Dining Area General | 1.4 |  | CS | Dining Area | General
| CS Electrical/Mechanical | 1.3 |  | CS | Electrical/Mechanical
| CS Food Preparation | 2.2 |  | CS | Food Preparation
| CS Inactive Storage General | 0.3 |  | CS | Inactive Storage | General
| CS Lobby All Other | 1.8 |  | CS | Lobby | All Other
| CS Lounge/Recreation | 1.4 |  | CS | Lounge/Recreation
| CS Office Enclosed | 1.5 |  | CS | Office | Enclosed
| CS Office Open Plan | 1.3 |  | CS | Office | Open Plan
| CS Restrooms | 1 |  | CS | Restrooms
Building Specific Space Types | SS Active Storage Hospital | 2.9 |  | SS | Active Storage | Hospital
| SS Active Storage Museum | 1.4 |  | SS | Active Storage | Museum
| SS Audience/Seating Area Convention Center | 0.5 |  | SS | Audience/Seating Area | Convention Center
| SS Audience/Seating Area Exercise Center | 0.5 |  | SS | Audience/Seating Area | Exercise Center
| SS Audience/Seating Area Gymnasium | 0.5 |  | SS | Audience/Seating Area | Gymnasium
| SS Audience/Seating Area Motion Picture Theater | 1.3 |  | SS | Audience/Seating Area | Motion Picture Theater
| SS Audience/Seating Area Penitentiary | 1.9 |  | SS | Audience/Seating Area | Penitentiary
| SS Audience/Seating Area Performing Arts Theater | 1.8 |  | SS | Audience/Seating Area | Performing Arts Theater
| SS Audience/Seating Area Religious Buildings | 3.2 |  | SS | Audience/Seating Area | Religious Buildings
| SS Audience/Seating Area Sports Arena | 0.5 |  | SS | Audience/Seating Area | Sports Arena
| SS Audience/Seating Area Transportation | 1 |  | SS | Audience/Seating Area | Transportation
| SS Automotive Service Repair | 1.4 |  | SS | Automotive | Service Repair
| SS Bank/Office Banking Activity Area | 2.4 |  | SS | Bank/Office | Banking Activity Area
| SS Classroom/Lecture/Training Penitentiary | 1.4 |  | SS | Classroom/Lecture/Training | Penitentiary
| SS Convention Center Exhibit Space | 3.3 |  | SS | Convention Center | Exhibit Space
| SS Corridor/Transition Hospital | 1.6 |  | SS | Corridor/Transition | Hospital
| SS Corridor/Transition Manufacturing Facility | 0.5 |  | SS | Corridor/Transition | Manufacturing Facility
| SS Courthouse/Police Station/Penitentiary Confinement Cells | 1.1 |  | SS | Courthouse/Police Station/Penitentiary | Confinement Cells
| SS Courthouse/Police Station/Penitentiary Courtroom | 2.1 |  | SS | Courthouse/Police Station/Penitentiary | Courtroom
| SS Courthouse/Police Station/Penitentiary Judges’ Chambers | 1.1 |  | SS | Courthouse/Police Station/Penitentiary | Judges’ Chambers
| SS Dining Area Bar Lounge/Leisure Dining | 1.2 |  | SS | Dining Area | Bar Lounge/Leisure Dining
| SS Dining Area Family Dining | 2.2 |  | SS | Dining Area | Family Dining
| SS Dining Area Hotel | 1 |  | SS | Dining Area | Hotel
| SS Dining Area Motel | 1.2 |  | SS | Dining Area | Motel
| SS Dormitory Living Quarters | 1.9 |  | SS | Dormitory | Living Quarters
| SS Dressing/Locker/Fitting Room | 0.8 |  | SS | Dressing/Locker/Fitting Room
| SS Fire Stations Engine Room | 0.9 |  | SS | Fire Stations | Engine Room
| SS Fire Stations Sleeping Quarters | 1.1 |  | SS | Fire Stations | Sleeping Quarters
| SS Gymnasium/Exercise Center Exercise Area | 1.1 |  | SS | Gymnasium/Exercise Center | Exercise Area
| SS Gymnasium/Exercise Center Playing Area | 1.9 |  | SS | Gymnasium/Exercise Center | Playing Area
| SS Hospital Emergency | 2.8 |  | SS | Hospital | Emergency
| SS Hospital Exam/Treatment | 1.6 |  | SS | Hospital | Exam/Treatment
| SS Hospital Laundry—Washing | 0.7 |  | SS | Hospital | Laundry—Washing
| SS Hospital Medical Supply | 3 |  | SS | Hospital | Medical Supply
| SS Hospital Nursery | 1 |  | SS | Hospital | Nursery
| SS Hospital Nurses’ Station | 1.8 |  | SS | Hospital | Nurses’ Station
| SS Hospital Operating Room | 7.6 |  | SS | Hospital | Operating Room
| SS Hospital Patient Room | 1.2 |  | SS | Hospital | Patient Room
| SS Hospital Pharmacy | 2.3 |  | SS | Hospital | Pharmacy
| SS Hospital Physical Therapy | 1.9 |  | SS | Hospital | Physical Therapy
| SS Hospital Radiology | 0.4 |  | SS | Hospital | Radiology
| SS Hospital Recovery | 2.6 |  | SS | Hospital | Recovery
| SS Hotel/Motel Guest Rooms | 2.5 |  | SS | Hotel/Motel | Guest Rooms
| SS Inactive Storage Museum | 1.4 |  | SS | Inactive Storage | Museum
| SS Laboratory | 1.8 |  | SS | Laboratory
| SS Library Card File and Cataloging | 1.4 |  | SS | Library | Card File and Cataloging
| SS Library Reading Area | 1.8 |  | SS | Library | Reading Area
| SS Library Stacks | 1.9 |  | SS | Library | Stacks
| SS Lobby Hotel | 1.7 |  | SS | Lobby | Hotel
| SS Lobby Motion Picture Theater | 0.8 |  | SS | Lobby | Motion Picture Theater
| SS Lobby Performing Arts Theater | 1.2 |  | SS | Lobby | Performing Arts Theater
| SS Manufacturing Control Room | 0.5 |  | SS | Manufacturing | Control Room
| SS Manufacturing Detailed Manufacturing | 6.2 |  | SS | Manufacturing | Detailed Manufacturing
| SS Manufacturing Equipment Room | 0.8 |  | SS | Manufacturing | Equipment Room
| SS Manufacturing High Bay (³25 ft Floor to Ceiling Height) | 3 |  | SS | Manufacturing | High Bay (³25 ft Floor to Ceiling Height)
| SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height) | 2.1 |  | SS | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height)
| SS Manufacturing Workshop | 2.5 |  | SS | Manufacturing | Workshop
| SS Museum General Exhibition | 1.6 |  | SS | Museum | General Exhibition
| SS Museum Restoration | 2.5 |  | SS | Museum | Restoration
| SS Parking Garage Attendant Only | 0.1 |  | SS | Parking Garage | Attendant Only
| SS Parking Garage Pedestrian | 0.2 |  | SS | Parking Garage | Pedestrian
| SS Post Office Sorting Area | 1.7 |  | SS | Post Office | Sorting Area
| SS Religious Buildings Fellowship Hall | 2.3 |  | SS | Religious Buildings | Fellowship Hall
| SS Religious Buildings Worship Pulpit, Choir | 5.2 |  | SS | Religious Buildings | Worship Pulpit, Choir
| SS Retail Mall Concourse | 1.8 |  | SS | Retail | Mall Concourse
| SS Retail Sales Area | 2.1 | Plus use-it-or-loose-it allowances per Section 9.6.3(c) | SS | Retail | Sales Area
| SS Sports Arena Court Sports Area | 4.3 |  | SS | Sports Arena | Court Sports Area
| SS Sports Arena Indoor Playing Field Area | 1.9 |  | SS | Sports Arena | Indoor Playing Field Area
| SS Sports Arena Ring Sports Area | 3.8 |  | SS | Sports Arena | Ring Sports Area
| SS Transportation Air/Train/Bus—Baggage Area | 1.3 |  | SS | Transportation | Air/Train/Bus—Baggage Area
| SS Transportation Airport—Concourse | 0.7 |  | SS | Transportation | Airport—Concourse
| SS Transportation Terminal—Ticket Counter | 1.8 |  | SS | Transportation | Terminal—Ticket Counter
| SS Warehouse Fine Material Storage | 1.6 |  | SS | Warehouse | Fine Material Storage
| SS Warehouse Medium/Bulky Material Storage | 1.1 |  | SS | Warehouse | Medium/Bulky Material Storage

## SSPC-90.1 (hidden)
Building Area Type | Schedule Index | Misc. Loads (W/ft²) | Ventilation rate (cfm/ft²) | Occupant Density (ft²/Person) | Sensible Occupant Heat Gain (Btu/h-person) | Latent Occupant Heat Gain (Btu/h-person) | Baseline Water Heating System from Table G3.1.1-2 | Notes
Automotive Facility | J | 1 | 0.25 | 143 | 375 | 625 | Gas Storage
Convention Center | H | 0.25 | 0.31 | 20 | 250 | 200 | Electric Resistance Storage
Courthouse | A | 0.25 | 0.41 | 14 | 250 | 200 | Electric Resistance Storage
Dining: Bar/Lounge/Leisure | B | 6 | 0.93 | 10 | 275 | 275 | Gas Storage
Dining: Cafeteria/Fast Food | B | 6 | 0.93 | 10 | 275 | 275 | Gas Storage
Dining: Family | B | 6 | 0.71 | 14 | 275 | 275 | Gas Storage
Dormitory | D | 0.6 | 0.11 | 100 | 250 | 200 | Gas Storage
Exercise Center | H | 0.5 | 0.26 | 100 | 710 | 1090 | Gas Storage
Fire Station | E | 1.5 | 0.21 | 33 | 250 | 200 | Gas Storage
Gymnasium | I | 0.5 | 0.3 | 33 | 710 | 1090 | Gas Storage
Health-Care Clinic | E | 2 | 0.47 | 200 | 250 | 200 | Gas Storage
Hospital | E | 2 | 0.47 | 200 | 250 | 200 | Gas Storage
Hotel | F | 1.11 | 0.08 | 250 | 250 | 200 | Gas Storage
Laboratory | M | 3.34 | 0.47 | 200 | 250 | 200 | Gas Storage | Added by Charles Eley
Library | C | 1.5 | 0.11 | 100 | 250 | 200 | Electric Resistance Storage
Manufacturing Facility | J | 1 | 0.25 | 143 | 580 | 870 | Gas Storage
Motel | F | 1.11 | 0.08 | 250 | 250 | 200 | Gas Storage
Motion Picture Theater | H | 0.54 | 1.19 | 7 | 225 | 105 | Electric Resistance Storage
Multifamily | D | 0.62 | 0.06 | 380 | 250 | 200 | Gas Storage
Museum | C | 1.5 | 0.36 | 25 | 250 | 200 | Electric Resistance Storage
Office | A | 0.75 | 0.09 | 200 | 250 | 200 | Electric Resistance Storage
Parking Garage | K | 0 | 0 | 0 | 250 | 200 | Electric Resistance Storage
Penitentiary | F | 0.5 | 0.25 | 40 | 250 | 200 | Gas Storage
Performing Arts Theater | H | 0.5 | 0.76 | 14 | 225 | 105 | Gas Storage
Police Station | E | 1.5 | 0.21 | 33 | 250 | 200 | Electric Resistance Storage
Post Office | A | 1 | 0.21 | 33 | 250 | 200 | Electric Resistance Storage
Religious Building | H | 0.96 | 0.66 | 8 | 245 | 155 | Electric Resistance Storage
Retail | C | 0.3 | 0.23 | 67 | 250 | 200 | Electric Resistance Storage
School/University | G | 1.39 | 0.47 | 40 | 250 | 200 | Gas Storage
Sports Arena | H | 1 | 0.3 | 0 | 245 | 105 | Gas Storage
Town Hall | A | 1 | 0.09 | 200 | 250 | 200 | Electric Resistance Storage
Transportation | E | 0.5 | 0.81 | 10 | 225 | 105 | Electric Resistance Storage
Warehouse | L | 0.24 | 0.06 | 0 | 275 | 475 | Electric Resistance Storage
Workshop | J | 1 | 0.25 | 143 | 635 | 965 | Gas Storage
No default | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | Included in Table G3.1.1-2
Use whole building data | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | Added by Charles Eley
Note: This data is published on the SSPC 90.1 website and is intended for use with the envelope trade-off method. Columns H and beyond are added to include information from Appendix G and other sources.
Gas Storage
Electric Resistance Storage
Note on C15: Charles Eley: From CBECS analysis
Note on D15: Charles Eley: Same as hospital, but fume hoods will add to this if they exist.
Note on E15: Charles Eley: Same as hospital
Note on F15: Charles Eley: Same as hospital
Note on G15: Charles Eley: Same as hospital
Note on H15: Charles Eley: Same as hospital

## CBECS-2003 (hidden)
[7 empty] | Plug Load Data (Note 1) | [8 empty] | Service Water Heating and Ventilation Rates from NREL (Note 2) | [5 empty] | Analysis based on Brandemuehl comments 3/8/2015
CBECS Classifications | Class | PBAcode | PLUScode | PBA | PBA Plus | CBECS 2003 Count | EPD Average | EPD Standard Dev | EPD Minimum | EPD Maximum | Area Weighted EPD | CBECS Weighted EPD | Csd | Pdmisc | Diversity | Mapping to NREL956 | Use Rate (gal/d-occ) | Storage Value (gal/occ) | Recovery Rate (gal/h-occ) | OA Ventilation (cfm/occ) | Mapping to PBAPlus | Mapping back to 90.1-2010 | Additional Mapping | Notes
Vacant PBA | PBA | 1 | 0 | Vacant | PBA | 134 | 0.60588 | 0.20634 | 0.54833 | 1.7787 | n.a. | 0.57608 | 2 | 0.54833 | 1 | Vacant | 0 | 1.585 | 0.88058 | 0 | Vacant | CS Electrical/Mechanical
Office PBA | PBA | 2 | 0 | Office | PBA | 976 | 1.7715 | 0.9197 | 0.77138 | 13.3373 | n.a. | 1.6721 | 2 | 0.77138 | 1 | Office/Professional > 30,000 ft² | 1.0039 | 1.585 | 0.88058 | 45.3486 | Administrative/professional office | BA Office
Laboratory PBA | PBA | 4 | 0 | Laboratory | PBA | 43 | 3.5035 | 0.55502 | 2.8907 | 5.5414 | n.a. | 3.3415 | 2 | 2.7881 | 1 | Laboratory | 10.0386 | 7.9252 | 8.8058 | 39.627 | Laboratory | CS Laboratory Classrooms | CS Laboratory Medical/Industrial/Research
Nonrefrigerated warehouse PBA | PBA | 5 | 0 | Nonrefrigerated warehouse | PBA | 473 | 0.36326 | 0.28901 | 0.18587 | 2.9225 | n.a. | 0.31395 | 2 | 0.18587 | 1 | Nonrefrigerated warehouse | 0.6076 | 1.585 | 0.88058 | 10.5955 | Non-refrigerated warehouse | CS Storage
Food sales PBA | PBA | 6 | 0 | Food sales | PBA | 125 | 0.90156 | 0.55336 | 0.47398 | 3.6233 | n.a. | 0.8243 | 2 | 0.47398 | 1 | Food sales | 5.0193 | 7.9252 | 4.4029 | 39.627 | Other food sales | #N/A | CS Sales Area | MJB4
Public order and safety PBA | PBA | 7 | 0 | Public order and safety | PBA | 85 | 1.5976 | 0.41435 | 1.1152 | 3.193 | n.a. | 1.5094 | 2 | 1.1152 | 1 | Public order and safety | 1.0039 | 1.585 | 0.88058 | 39.627 | Other public order and safety | #N/A
Outpatient health care PBA | PBA | 8 | 0 | Outpatient health care | PBA | 144 | 1.3115 | 0.49893 | 0.56949 | 3.6766 | n.a. | 1.2202 | 2 | 0.54833 | 1 | Outpatient health care | 3.0116 | 4.7551 | 2.6417 | 39.627 | Clinic/other outpatient health | BA Healthcare Clinic
Refrigerated warehouse PBA | PBA | 11 | 0 | Refrigerated warehouse | PBA | 20 | 0.18669 | 0.081783 | 0.092937 | 0.32879 | n.a. | 0.17039 | 2 | 0.092937 | 1 | Refrigerated warehouse | 0.6076 | 1.3209 | 0.88058 | 4.2382 | Refrigerated warehouse | SS Warehouse Medium/Bulky Material Storage |  | MJB17
Religious worship PBA | PBA | 12 | 0 | Religious worship | PBA | 311 | 0.31376 | 0.084934 | 0.21933 | 0.73113 | n.a. | 0.29845 | 2 | 0.54833 | 0.4 | Religious worship | 0.26417 | 0.52835 | 0.44029 | 39.627 | Religious worship | BA Religious Building
Public assembly PBA | PBA | 13 | 0 | Public assembly | PBA | 279 | 0.84604 | 0.45381 | 0.54833 | 5.6039 | n.a. | 0.74761 | 2 | 0.54833 | 1 | Public assembly | 0.26417 | 0.52835 | 0.44029 | 39.627 | Social/meeting | BA Convention Center |  | MJB9
Education PBA | PBA | 14 | 0 | Education | PBA | 649 | 0.72499 | 0.74687 | 0.1487 | 14.4147 | n.a. | 0.68748 | 2 | 0.1487 | 1 | Education college | 0.6076 | 1.585 | 0.88058 | 13.3503 | High school | BA School/University
Food service PBA | PBA | 15 | 0 | Food service | PBA | 242 | 1.3937 | 0.5574 | 0.93705 | 4.8348 | n.a. | 1.2903 | 2 | 0.92937 | 1 | Food service | 10.0386 | 15.8504 | 8.8058 | 39.627 | Restaurant/cafeteria | #N/A | CS Food Preparation
Inpatient health care PBA | PBA | 16 | 0 | Inpatient health care | PBA | 217 | 1.3057 | 0.41515 | 0.82811 | 4.3919 | n.a. | 1.2488 | 2 | 0.76208 | 1 | Inpatient health care | 3.0116 | 4.7551 | 2.6417 | 39.627 | Hospital/inpatient health | BA Hospital |  | MJB15
Nursing PBA | PBA | 17 | 0 | Nursing | PBA | 73 | 1.5078 | 0.41008 | 1.1354 | 3.3112 | n.a. | 1.4046 | 2 | 1.1152 | 1 | Skilled nursing | 3.0116 | 4.7551 | 2.6417 | 39.627 | Nursing home/assisted living | #N/A | SS Dormitory Living Quarters | MJB12
Lodging PBA | PBA | 18 | 0 | Lodging | PBA | 260 | 1.7669 | 0.96622 | 1.1152 | 8.4775 | n.a. | 1.5925 | 2 | 0.2974 | 1 | Lodging 20-100 rooms | 14.0276 | 13.2086 | 13.2086 | 39.627 | Hotel | #N/A | SS Dormitory Living Quarters
Strip shopping mall PBA | PBA | 23 | 0 | Strip shopping mall | PBA | 349 | 0 | 0 | 0 | 0 | n.a. | 0 | 2 | 0.54833 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 | Strip shopping mall | #N/A | BA Retail
Enclosed mall PBA | PBA | 24 | 0 | Enclosed mall | PBA | 46 | 0 | 0 | 0 | 0 | n.a. | 0 | 2 | 0.54833 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 | Enclosed mall | #N/A | BA Retail | MJB18
Retail (except Malls) PBA | PBA | 25 | 0 | Retail (except Malls) | PBA | 355 | 0.76353 | 0.54981 | 0.34387 | 3.9329 | n.a. | 0.70235 | 2 | 0.34387 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 | Retail store | BA Retail
Service (except Food) PBA | PBA | 26 | 0 | Service (except Food) | PBA | 370 | 0.52394 | 0.43553 | 0.18587 | 5.4419 | n.a. | 0.49073 | 2 | 0.54833 | 1 | Service | 1.0039 | 1.585 | 0.88058 | 39.627 | Repair shop | #N/A
Other PBA | PBA | 91 | 0 | Other | PBA | 64 | 1.2041 | 5.2179 | 0.18587 | 42.1524 | n.a. | 1.2743 | 2 | 0.54833 | 1 | Other | 1.0039 | 1.585 | 0.88058 | 39.627 | Other | CS Atrium First 40 ft in Height
Vacant Vacant | Plus | 1 | 1 | Vacant | Vacant | 134 | 0.60588 | 0.20634 | 0.54833 | 1.7787 | n.a. | 0.57608 | 2 | 0.54833 | 1 | Vacant | 0 | 1.585 | 0.88058 | 0 |  | #N/A | CS Electrical/Mechanical
Office Administrative/professional office | Plus | 2 | 2 | Office | Administrative/professional office | 520 | 1.8036 | 1.018 | 0.79578 | 13.3373 | n.a. | 1.676 | 2 | 0.77138 | 1 | Office/Professional > 30,000 ft² | 1.0039 | 1.585 | 0.88058 | 45.3486 |  | #N/A | BA Office
Office Bank/other financial | Plus | 2 | 3 | Office | Bank/other financial | 67 | 1.959 | 0.77265 | 0.84998 | 4.2061 | n.a. | 1.7201 | 2 | 0.77138 | 1 | Office/Professional < 30,000 ft² | 1.0039 | 1.585 | 0.88058 | 55.3083 |  | SS Bank/Office Banking Activity Area
Office Government office | Plus | 2 | 4 | Office | Government office | 149 | 1.6852 | 0.79688 | 0.7932 | 7.3632 | n.a. | 1.669 | 2 | 0.77138 | 1 | Office/Professional > 30,000 ft² | 1.0039 | 1.585 | 0.88058 | 45.3486 |  | BA Courthouse |  | MJB2
Office Medical office (non-diagnostic) | Plus | 2 | 5 | Office | Medical office (non-diagnostic) | 27 | 1.7449 | 0.67462 | 0.78639 | 3.4808 | n.a. | 1.613 | 2 | 0.77138 | 1 | Outpatient health care | 3.0116 | 4.7551 | 2.6417 | 39.627 |  | #N/A | BA Office
Office Mixed-use office | Plus | 2 | 6 | Office | Mixed-use office | 164 | 1.6954 | 0.81225 | 0.80793 | 9.3422 | n.a. | 1.641 | 2 | 0.77138 | 1 | Office/Professional < 30,000 ft² | 1.0039 | 1.585 | 0.88058 | 55.3083 |  | #N/A | BA Office
Office Other office | Plus | 2 | 7 | Office | Other office | 49 | 1.7062 | 0.77635 | 0.77138 | 4.0282 | n.a. | 1.6987 | 2 | 0.77138 | 1 | Office/Professional < 30,000 ft² | 1.0039 | 1.585 | 0.88058 | 55.3083 |  | #N/A | BA Office
Laboratory Laboratory | Plus | 4 | 8 | Laboratory | Laboratory | 43 | 3.5035 | 0.55502 | 2.8907 | 5.5414 | n.a. | 3.3415 | 2 | 2.7881 | 1 | Laboratory | 10.0386 | 7.9252 | 8.8058 | 39.627 |  | #N/A | CS Laboratory Medical/Industrial/Research | MJB3
Nonrefrigerated warehouse Distribution/shipping center | Plus | 5 | 9 | Nonrefrigerated warehouse | Distribution/shipping center | 226 | 0.41678 | 0.28633 | 0.18587 | 2.16 | n.a. | 0.34481 | 2 | 0.18587 | 1 | Nonrefrigerated warehouse | 0.6076 | 1.585 | 0.88058 | 10.5955 |  | BA Manufacturing Facility |  | MJB16
Nonrefrigerated warehouse Non-refrigerated warehouse | Plus | 5 | 10 | Nonrefrigerated warehouse | Non-refrigerated warehouse | 163 | 0.35607 | 0.26558 | 0.18587 | 1.8909 | n.a. | 0.30231 | 2 | 0.18587 | 1 | Nonrefrigerated warehouse | 0.6076 | 1.585 | 0.88058 | 10.5955 |  | BA Warehouse
Nonrefrigerated warehouse Self-storage | Plus | 5 | 11 | Nonrefrigerated warehouse | Self-storage | 84 | 0.23321 | 0.30011 | 0.18587 | 2.9225 | n.a. | 0.21318 | 2 | 0.18587 | 1 | Nonrefrigerated warehouse | 0.6076 | 1.585 | 0.88058 | 10.5955 |  | #N/A | BA Warehouse
Food sales Convenience store | Plus | 6 | 12 | Food sales | Convenience store | 24 | 1.1326 | 0.72878 | 0.47398 | 2.8006 | n.a. | 0.98457 | 2 | 0.47398 | 1 | Food sales | 5.0193 | 7.9252 | 4.4029 | 39.627 |  | #N/A | CS Sales Area | MJB4
Food sales Convenience store with gas station | Plus | 6 | 13 | Food sales | Convenience store with gas station | 32 | 0.93191 | 0.58645 | 0.5109 | 2.9535 | n.a. | 0.8612 | 2 | 0.47398 | 1 | Food sales | 5.0193 | 7.9252 | 4.4029 | 39.627 |  | #N/A | CS Sales Area | MJB4
Food sales Grocery store/food market | Plus | 6 | 14 | Food sales | Grocery store/food market | 63 | 0.82563 | 0.45533 | 0.47398 | 3.6233 | n.a. | 0.79692 | 2 | 0.47398 | 1 | Food sales | 5.0193 | 7.9252 | 4.4029 | 39.627 |  | #N/A | CS Sales Area | MJB4
Food sales Other food sales | Plus | 6 | 15 | Food sales | Other food sales | 6 | 0.61269 | 0.11234 | 0.47398 | 0.73252 | n.a. | 0.65193 | 2 | 0.47398 | 1 | Food sales | 5.0193 | 7.9252 | 4.4029 | 39.627 |  | #N/A | CS Sales Area | MJB4
Public order and safety Fire station/police station | Plus | 7 | 16 | Public order and safety | Fire station/police station | 47 | 1.6273 | 0.44885 | 1.1152 | 3.193 | n.a. | 1.5404 | 2 | 1.1152 | 1 | Public order and safety | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Fire Station |  | MJB5
Public order and safety Other public order and safety | Plus | 7 | 17 | Public order and safety | Other public order and safety | 38 | 1.5608 | 0.36984 | 1.1493 | 2.6892 | n.a. | 1.4928 | 2 | 1.1152 | 1 | Public order and safety | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Penitentiary |  | MJB6
Outpatient health care Medical office (diagnostic) | Plus | 8 | 18 | Outpatient health care | Medical office (diagnostic) | 52 | 1.4249 | 0.61201 | 0.60818 | 3.6766 | n.a. | 1.2167 | 2 | 0.54833 | 1 | Outpatient health care | 3.0116 | 4.7551 | 2.6417 | 39.627 |  | #N/A | BA Healthcare Clinic
Outpatient health care Clinic/other outpatient health | Plus | 8 | 19 | Outpatient health care | Clinic/other outpatient health | 92 | 1.2475 | 0.41203 | 0.56949 | 2.7257 | n.a. | 1.2225 | 2 | 0.54833 | 1 | Outpatient health care | 3.0116 | 4.7551 | 2.6417 | 39.627 |  | #N/A | BA Healthcare Clinic
Refrigerated warehouse Refrigerated warehouse | Plus | 11 | 20 | Refrigerated warehouse | Refrigerated warehouse | 20 | 0.18669 | 0.081783 | 0.092937 | 0.32879 | n.a. | 0.17039 | 2 | 0.092937 | 1 | Refrigerated warehouse | 0.6076 | 1.3209 | 0.88058 | 4.2382 |  | #N/A | BA Warehouse | Not the same.
Religious worship Religious worship | Plus | 12 | 21 | Religious worship | Religious worship | 311 | 0.31376 | 0.084934 | 0.21933 | 0.73113 | n.a. | 0.29845 | 2 | 0.54833 | 0.4 | Religious worship | 0.26417 | 0.52835 | 0.44029 | 39.627 |  | #N/A | BA Performing Arts Theater
Public assembly Entertainment/culture | Plus | 13 | 22 | Public assembly | Entertainment/culture | 44 | 0.74563 | 0.27703 | 0.54833 | 1.9662 | n.a. | 0.74485 | 2 | 0.54833 | 1 | Public assembly | 0.26417 | 0.52835 | 0.44029 | 39.627 |  | BA Motion Picture Theater |  | MJB7
Public assembly Library | Plus | 13 | 23 | Public assembly | Library | 36 | 1.0572 | 0.40368 | 0.61232 | 2.8652 | n.a. | 0.93723 | 2 | 0.54833 | 1 | Public assembly | 0.26417 | 0.52835 | 0.44029 | 39.627 |  | BA Library
Public assembly Recreation | Plus | 13 | 24 | Public assembly | Recreation | 92 | 0.71634 | 0.24698 | 0.54833 | 2.654 | n.a. | 0.67425 | 2 | 0.54833 | 1 | Public assembly | 0.26417 | 0.52835 | 0.44029 | 39.627 |  | BA Exercise Center |  | MJB8
Public assembly Social/meeting | Plus | 13 | 25 | Public assembly | Social/meeting | 76 | 0.96244 | 0.67723 | 0.54833 | 5.6039 | n.a. | 0.73324 | 2 | 0.54833 | 1 | Public assembly | 0.26417 | 0.52835 | 0.44029 | 39.627 |  | CS Conference/Meeting/Multipurpose
Public assembly Other public assembly | Plus | 13 | 26 | Public assembly | Other public assembly | 31 | 0.84298 | 0.34991 | 0.54833 | 2.4463 | n.a. | 0.76225 | 2 | 0.54833 | 1 | Public assembly | 0.26417 | 0.52835 | 0.44029 | 39.627 |  | SS Hotel/Highway Lodging Hotel Lobby |  | MJB10
Education College/university | Plus | 14 | 27 | Education | College/university | 88 | 1.2356 | 0.61797 | 0.76799 | 4.2853 | n.a. | 1.4895 | 1.6 | 0.74349 | 1 | Education college | 0.6076 | 1.585 | 0.88058 | 13.3503 |  | #N/A | BA School/University
Education Elementary/middle school | Plus | 14 | 28 | Education | Elementary/middle school | 330 | 0.64799 | 0.86593 | 0.1487 | 14.4147 | n.a. | 0.55367 | 2 | 0.1487 | 1 | Education elementary | 0.6076 | 1.585 | 0.88058 | 13.3503 |  | #N/A | BA School/University
Education High school | Plus | 14 | 29 | Education | High school | 126 | 0.64403 | 0.53807 | 0.1487 | 3.7737 | n.a. | 0.5549 | 2 | 0.1487 | 1 | Education high school | 1.7964 | 3.1701 | 1.7612 | 13.3503 |  | #N/A | BA School/University
Education Preschool/daycare | Plus | 14 | 30 | Education | Preschool/daycare | 46 | 0.69039 | 0.40273 | 0.16291 | 1.6793 | n.a. | 0.47671 | 2 | 0.1487 | 1 | Education elementary | 0.6076 | 1.585 | 0.88058 | 13.3503 |  | #N/A | BA School/University
Education Other classroom education | Plus | 14 | 31 | Education | Other classroom education | 59 | 0.59397 | 0.44073 | 0.18587 | 2.4938 | n.a. | 0.58913 | 2 | 0.18587 | 1 | Education college | 0.6076 | 1.585 | 0.88058 | 13.3503 |  | CS Classroom/Lecture/Training
Food service Fast food | Plus | 15 | 32 | Food service | Fast food | 54 | 1.4434 | 0.57809 | 0.973 | 3.6085 | n.a. | 1.3684 | 2 | 0.92937 | 1 | Food service | 10.0386 | 15.8504 | 8.8058 | 39.627 |  | BA Dining: Cafeteria/Fast Food
Food service Restaurant/cafeteria | Plus | 15 | 33 | Food service | Restaurant/cafeteria | 145 | 1.3527 | 0.52858 | 0.93705 | 4.8348 | n.a. | 1.263 | 2 | 0.92937 | 1 | Food service | 10.0386 | 15.8504 | 8.8058 | 39.627 |  | BA Dining: Family
Food service Other food service | Plus | 15 | 34 | Food service | Other food service | 43 | 1.4692 | 0.62316 | 0.93897 | 3.5094 | n.a. | 1.3161 | 2 | 0.92937 | 1 | Food service | 10.0386 | 15.8504 | 8.8058 | 39.627 |  | BA Dining: Bar Lounge/Leisure |  | MJB11
Inpatient health care Hospital/inpatient health | Plus | 16 | 35 | Inpatient health care | Hospital/inpatient health | 217 | 1.3057 | 0.41515 | 0.82811 | 4.3919 | n.a. | 1.2488 | 2 | 0.76208 | 1 | Inpatient health care | 3.0116 | 4.7551 | 2.6417 | 39.627 |  | SS Hospital Corridor/Transition
Nursing Nursing home/assisted living | Plus | 17 | 36 | Nursing | Nursing home/assisted living | 73 | 1.5078 | 0.41008 | 1.1354 | 3.3112 | n.a. | 1.4046 | 2 | 1.1152 | 1 | Skilled nursing | 3.0116 | 4.7551 | 2.6417 | 39.627 |  | SS Hotel/Highway Lodging Hotel Guest Rooms
Lodging Dormitory/fraternity/sorority | Plus | 18 | 37 | Lodging | Dormitory/fraternity/sorority | 37 | 1.9604 | 0.68006 | 1.1152 | 3.9056 | n.a. | 1.9561 | 2 | 0.2974 | 1 | Lodging 20-100 rooms | 14.0276 | 13.2086 | 13.2086 | 39.627 |  | BA Dormitory
Lodging Hotel | Plus | 18 | 38 | Lodging | Hotel | 86 | 1.6139 | 0.59482 | 1.1348 | 4.8452 | n.a. | 1.5641 | 2 | 0.2974 | 1 | Lodging 20-100 rooms | 14.0276 | 13.2086 | 13.2086 | 39.627 |  | BA Hotel
Lodging Motel or inn | Plus | 18 | 39 | Lodging | Motel or inn | 109 | 1.7929 | 1.1505 | 1.1152 | 8.4775 | n.a. | 1.5696 | 2 | 0.2974 | 1 | Lodging 20-100 rooms | 14.0276 | 13.2086 | 13.2086 | 39.627 |  | SS Hotel/Highway Lodging Highway Lodging Guest Rooms
Lodging Other lodging | Plus | 18 | 40 | Lodging | Other lodging | 28 | 1.8798 | 1.3374 | 1.1152 | 7.1142 | n.a. | 1.4245 | 2 | 0.2974 | 1 | Lodging 20-100 rooms | 14.0276 | 13.2086 | 13.2086 | 39.627 |  | BA Multifamily |  | MJB13, MJB19
Strip shopping mall Strip shopping mall | Plus | 23 | 50 | Strip shopping mall | Strip shopping mall | 349 | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | 2 | 0.54833 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 |  | #N/A | BA Retail
Enclosed mall Enclosed mall | Plus | 24 | 51 | Enclosed mall | Enclosed mall | 46 | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | 2 | 0.54833 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 |  | #N/A | BA Retail | MJB18
Retail (except Malls) Vehicle dealership/showroom | Plus | 25 | 41 | Retail (except Malls) | Vehicle dealership/showroom | 39 | 1.6643 | 0.52427 | 1.126 | 3.8016 | n.a. | 1.5444 | 2 | 0.34387 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 |  | #N/A | BA Retail
Retail (except Malls) Retail store | Plus | 25 | 42 | Retail (except Malls) | Retail store | 291 | 0.62919 | 0.40891 | 0.34387 | 3.9329 | n.a. | 0.54928 | 2 | 0.34387 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 |  | SS Retail Sales Area
Retail (except Malls) Other retail | Plus | 25 | 43 | Retail (except Malls) | Other retail | 25 | 0.92191 | 0.66301 | 0.38227 | 2.6872 | n.a. | 0.82157 | 2 | 0.34387 | 1 | Retail | 0.6076 | 1.0567 | 0.88058 | 39.627 |  | CS Dressing/Fitting Room Performing Arts Theater
Service (except Food) Post office/postal center | Plus | 26 | 44 | Service (except Food) | Post office/postal center | 23 | 0.93007 | 0.46103 | 0.54833 | 2.6029 | n.a. | 0.90907 | 2 | 0.54833 | 1 | Service | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Post Office
Service (except Food) Repair shop | Plus | 26 | 45 | Service (except Food) | Repair shop | 44 | 0.47709 | 0.19845 | 0.18587 | 0.99769 | n.a. | 0.42834 | 2 | 0.54833 | 1 | Service | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Workshop
Service (except Food) Vehicle service/repair shop | Plus | 26 | 46 | Service (except Food) | Vehicle service/repair shop | 125 | 0.54789 | 0.35298 | 0.18587 | 2.5372 | n.a. | 0.50325 | 2 | 0.54833 | 1 | Service | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Automotive Facility
Service (except Food) Vehicle storage/maintenance | Plus | 26 | 47 | Service (except Food) | Vehicle storage/maintenance | 99 | 0.34856 | 0.20482 | 0.18587 | 1.3525 | n.a. | 0.32657 | 2 | 0.54833 | 1 | Service | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Parking Garage
Service (except Food) Other service | Plus | 26 | 48 | Service (except Food) | Other service | 79 | 0.61365 | 0.68335 | 0.18587 | 5.4419 | n.a. | 0.51912 | 2 | 0.54833 | 1 | Service | 1.0039 | 1.585 | 0.88058 | 39.627 |  | BA Transportation |  | MJB14
Other Other | Plus | 91 | 49 | Other | Other | 64 | 1.2041 | 5.2179 | 0.18587 | 42.1524 | n.a. | 1.2743 | 2 | 0.54833 | 1 | Other | 1.0039 | 1.585 | 0.88058 | 39.627 |  | #N/A
No default | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a.
Use whole building data | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | n.a. | n.a. | n.a. | n.a. | n.a.
Notes:
1. These EPD values were calculated on a separate spreadsheet (see 'COMNET Plug Load Calcs (Rev 3).xlsx'). For each CBECS 2003 site, the EPA is
calculated using the procedures based on the NREL methodology technical report (NRL/TP-550-41956). However, the average equipment power values used in | [21 empty] | Lookup Range for Above Analysis
the NREL report were updated to reflect the shift from CRTs to flat screen monitors and other changes that have occurred since the report was originally | [21 empty] | CBECS Classifications | COMNET/90.1 Classifications
published. The new data were taken from the HOF 2013. See 150928 Plug Loads TSD.pff. | [21 empty] | Service (except Food) Vehicle service/repair shop | BA Automotive Facility
[22 empty] | Public assembly PBA | BA Convention Center
2. The source of this information is taken from Table C39 and Table C40, NREL/TP-550-41956. | [21 empty] | Office Government office | BA Courthouse
[22 empty] | Food service Other food service | BA Dining: Bar Lounge/Leisure
[22 empty] | Food service Fast food | BA Dining: Cafeteria/Fast Food
[22 empty] | Food service Restaurant/cafeteria | BA Dining: Family
[22 empty] | Lodging Dormitory/fraternity/sorority | BA Dormitory
[22 empty] | Public assembly Recreation | BA Exercise Center
[22 empty] | Public order and safety Fire station/police station | BA Fire Station
[22 empty] | Public assembly Recreation | BA Gymnasium
[22 empty] | Outpatient health care PBA | BA Healthcare Clinic
[22 empty] | Inpatient health care PBA | BA Hospital
[22 empty] | Lodging Hotel | BA Hotel
[22 empty] | Public assembly Library | BA Library
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | BA Manufacturing Facility
[22 empty] | Lodging Hotel | BA Motel
[22 empty] | Public assembly Entertainment/culture | BA Motion Picture Theater
[22 empty] | Lodging Other lodging | BA Multifamily
[22 empty] | Public assembly Entertainment/culture | BA Museum
[22 empty] | Office PBA | BA Office
[22 empty] | Service (except Food) Vehicle storage/maintenance | BA Parking Garage
[22 empty] | Public order and safety Other public order and safety | BA Penitentiary
[22 empty] | Public assembly Entertainment/culture | BA Performing Arts Theater
[22 empty] | Public order and safety Fire station/police station | BA Police Station
[22 empty] | Service (except Food) Post office/postal center | BA Post Office
[22 empty] | Religious worship PBA | BA Religious Building
[22 empty] | Retail (except Malls) PBA | BA Retail
[22 empty] | Education PBA | BA School/University
[22 empty] | Public assembly PBA | BA Sports Arena
[22 empty] | Public assembly PBA | BA Town Hall
[22 empty] | Service (except Food) Other service | BA Transportation
[22 empty] | Nonrefrigerated warehouse Non-refrigerated warehouse | BA Warehouse
[22 empty] | Service (except Food) Repair shop | BA Workshop
[22 empty] | Other PBA | CS Atrium First 40 ft in Height
[22 empty] | Other PBA | CS Atrium Height Above 40 ft
[22 empty] | Public assembly PBA | CS Audience Seating Permanent Auditorium
[22 empty] | Public assembly PBA | CS Audience Seating Permanent Motion Picture Theater
[22 empty] | Public assembly PBA | CS Audience Seating Permanent Performing Arts Theater
[22 empty] | Service (except Food) Vehicle service/repair shop | SS Automotive Service/Repair
[22 empty] | Office Bank/other financial | SS Bank/Office Banking Activity Area
[22 empty] | Education Other classroom education | CS Classroom/Lecture/Training
[22 empty] | Public assembly Social/meeting | CS Conference/Meeting/Multipurpose
[22 empty] | Public assembly PBA | SS Convention Center Audience Seating
[22 empty] | Public assembly PBA | SS Convention Center Exhibit Space
[22 empty] | Other PBA | CS Corridor/Transition
[22 empty] | Public order and safety Other public order and safety | SS Courthouse/Police Station/Penitentiary Confinement Cells
[22 empty] | Public order and safety Other public order and safety | SS Courthouse/Police Station/Penitentiary Courtroom
[22 empty] | Public order and safety Other public order and safety | SS Courthouse/Police Station/Penitentiary Judges’ Chambers
[22 empty] | Food service Restaurant/cafeteria | CS Dining Area General
[22 empty] | Food service Restaurant/cafeteria | CS Dining Area Bar Lounge/Leisure Dining
[22 empty] | Food service Other food service | CS Dining Area Family Dining
[22 empty] | Lodging Dormitory/fraternity/sorority | SS Dormitory Living Quarters
[22 empty] | Retail (except Malls) Other retail | CS Dressing/Fitting Room Performing Arts Theater
[22 empty] | Vacant PBA | CS Electrical/Mechanical
[22 empty] | Vacant PBA | CS Electrical/Mechanical
[22 empty] | Public order and safety Fire station/police station | SS Fire Stations Engine Room
[22 empty] | Public order and safety Fire station/police station | SS Fire Stations Sleeping Quarters
[22 empty] | Food service Other food service | CS Food Preparation
[22 empty] | Public assembly Recreation | SS Gymnasium/Fitness Center Fitness Area
[22 empty] | Public assembly Recreation | SS Gymnasium/Fitness Center Gymnasium Audience Seating
[22 empty] | Public assembly Recreation | SS Gymnasium/Fitness Center Playing Area
[22 empty] | Nursing Nursing home/assisted living | SS Hotel/Highway Lodging Hotel Guest Rooms
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Corridor/Transition
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Emergency
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Exam/Treatment
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Laundry/Washing
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Lounge/Recreation
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Medical Supply
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Nursery
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Nurses’ Station
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Operating Room
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Patient Room
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Pharmacy
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Physical Therapy
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Radiology/Imaging
[22 empty] | Inpatient health care Hospital/inpatient health | SS Hospital Recovery
[22 empty] | Food service Restaurant/cafeteria | SS Hotel/Highway Lodging Hotel Dining
[22 empty] | Lodging Hotel | SS Hotel/Highway Lodging Hotel Guest Rooms
[22 empty] | Public assembly Other public assembly | SS Hotel/Highway Lodging Hotel Lobby
[22 empty] | Food service Restaurant/cafeteria | SS Hotel/Highway Lodging Highway Lodging Dining
[22 empty] | Lodging Motel or inn | SS Hotel/Highway Lodging Highway Lodging Guest Rooms
[22 empty] | Laboratory PBA | CS Laboratory Classrooms
[22 empty] | Laboratory PBA | CS Laboratory Medical/Industrial/Research
[22 empty] | Service (except Food) Other service | SS Hospital Laundry/Washing
[22 empty] | Public assembly Library | SS Library Card File and Cataloging
[22 empty] | Public assembly Library | SS Library Reading Area
[22 empty] | Public assembly Library | SS Library Stacks
[22 empty] | Public assembly Other public assembly | CS Lobby General
[22 empty] | Public assembly Other public assembly | CS Lobby Elevator
[22 empty] | Public assembly Entertainment/culture | CS Lobby Motion Picture Theater
[22 empty] | Public assembly Entertainment/culture | CS Lobby Performing Arts Theater
[22 empty] | Other PBA | CS Locker Room
[22 empty] | Public assembly Recreation | CS Lounge/Recreation
[22 empty] | Office PBA | CS Electrical/Mechanical
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Corridor/Transition
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Detailed Manufacturing
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Equipment Room
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Extra High Bay (>50 ft Floor to Ceiling Height)
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing High Bay (25–50 ft Floor to Ceiling Height)
[22 empty] | Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height)
[22 empty] | Public assembly Entertainment/culture | SS Museum General Exhibition
[22 empty] | Service (except Food) Repair shop | SS Museum Restoration
[22 empty] | Nonrefrigerated warehouse PBA | CS Storage
[22 empty] | Nonrefrigerated warehouse PBA | CS Storage
[22 empty] | Office PBA | CS Office Enclosed
[22 empty] | Office PBA | CS Office Open Plan
[22 empty] | Service (except Food) Vehicle storage/maintenance | SS Parking Garage Garage Area
[22 empty] | Public assembly Other public assembly | SS Courthouse/Police Station/Penitentiary Penitentiary Audience Seating
[22 empty] | Education Other classroom education | SS Courthouse/Police Station/Penitentiary Penitentiary Classroom
[22 empty] | Food service Restaurant/cafeteria | SS Courthouse/Police Station/Penitentiary Penitentiary Dining
[22 empty] | Service (except Food) Post office/postal center | SS Post Office Sorting Area
[22 empty] | Religious worship PBA | SS Religious Buildings Audience Seating
[22 empty] | Religious worship PBA | SS Religious Buildings Fellowship Hall
[22 empty] | Religious worship PBA | SS Religious Buildings Worship Pulpit, Choir
[22 empty] | Other PBA | CS Restrooms
[22 empty] | Other PBA | SS Retail Dressing/Fitting Room
[22 empty] | Retail (except Malls) Other retail | SS Retail Mall Concourse
[22 empty] | Retail (except Malls) Retail store | SS Retail Sales Area
[22 empty] | Public assembly Other public assembly | SS Sports Arena Audience Seating
[22 empty] | Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 1
[22 empty] | Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 2
[22 empty] | Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 3
[22 empty] | Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 4
[22 empty] | Public assembly Recreation | SS Sports Arena Indoor Sports Fields
[22 empty] | Public assembly Recreation | SS Sports Arena Ring Sports Arena
[22 empty] | Other PBA | CS Stairway
[22 empty] | Nonrefrigerated warehouse PBA | CS Storage
[22 empty] | Nonrefrigerated warehouse PBA | CS Storage
[22 empty] | Public assembly Other public assembly | SS Transportation Air/Train/Bus—Baggage Area
[22 empty] | Public assembly Other public assembly | SS Transportation Airport—Concourse
[22 empty] | Public assembly Other public assembly | SS Transportation Audience Seating
[22 empty] | Public assembly Other public assembly | SS Transportation Terminal—Ticket Counter
[22 empty] | Nonrefrigerated warehouse PBA | SS Warehouse Fine Material Storage
[22 empty] | Nonrefrigerated warehouse PBA | SS Warehouse Medium/Bulky Material Storage
[22 empty] | Refrigerated warehouse PBA | SS Warehouse Medium/Bulky Material Storage
[22 empty] | Service (except Food) Repair shop | CS Workshop, General
Not assiogned
CS Sales Area
Note on M2: Charles Eley: This is the value that is used.

## CEUS (hidden)
|  |  |  | Electric Energy (kWh/ft²-y) Source: CEUS Table E-3 | [13 empty] | Gas Energy (kBtu/ft²-y)
Building Type | Gas Process (Btu/h-ft²) | Refrigeration (W/ft²) | Floor Stock (ft²) | Total | Heat | Cool | Vent | Refrig | Water | Cooking | Interior Lights | Exterior Lights | Office Equipment | Misc. | Air Compressors | Motors | Other Process | Total | Heat | Cool | Water | Cooking | Misc. | Other Process
All Commercial | 0.90183 | 0.2089 | 4920114 | 13.63 | 0.22 | 2.04 | 1.63 | 1.83 | 0.12 | 0.57 | 3.92 | 0.8 | 0.97 | 0.8 | 0.04 | 0.57 | 0.13 | 25.99 | 9.5 | 0.4 | 8.3 | 5.9 | 0.5 | 1.5
Small Office | 0.022831 | 0.06621 | 361584 | 13.1 | 0.2 | 2.61 | 1.29 | 0.58 | 0.25 | 0.1 | 3.83 | 0.95 | 2.19 | 0.78 | 0 | 0.22 | 0.1 | 10.54 | 8.6 | 0 | 1.7 | 0.1 | 0 | 0.1
Large Office | 0.17123 | 0.046804 | 660429 | 17.7 | 0.49 | 3.57 | 3.06 | 0.41 | 0.12 | 0.12 | 4.46 | 0.49 | 3.58 | 0.58 | 0.03 | 0.72 | 0.09 | 21.93 | 17.2 | 0.5 | 2.6 | 0.2 | 0.1 | 1.2
Restaurant | 17.5342 | 1.1267 | 148892 | 40.2 | 0.05 | 5.76 | 3.24 | 9.87 | 0.38 | 10.38 | 6.45 | 2.02 | 0.63 | 1.13 | 0.01 | 0.27 | 0.02 | 209.98 | 7.7 | 0 | 48.6 | 153.3 | 0 | 0.3
Retail | 0.091324 | 0.11758 | 702053 | 14.06 | 0.08 | 2.21 | 1.81 | 1.03 | 0.14 | 0.22 | 6.05 | 0.92 | 0.49 | 0.69 | 0.05 | 0.29 | 0.09 | 4.62 | 3 | 0 | 0.8 | 0.5 | 0.3 | 0
Food Store | 1.1872 | 2.5594 | 144209 | 40.99 | 0.08 | 2.88 | 2.58 | 22.42 | 0.14 | 1.85 | 8.55 | 0.95 | 0.37 | 0.95 | 0.01 | 0.18 | 0.04 | 27.6 | 9.5 | 0 | 7.7 | 10.3 | 0 | 0.1
Refrigerated Warehouse | 0.45662 | 1.5342 | 95540 | 20.02 | 0.02 | 0.33 | 0.24 | 13.44 | 0.03 | 0.04 | 2.74 | 0.35 | 0.17 | 0.57 | 0.04 | 1.82 | 0.23 | 5.6 | 0.8 | 0 | 0.8 | 1.2 | 0 | 2.8
Unrefrigerated Warehouse | 0 | 0.031963 | 554166 | 4.45 | 0.04 | 0.33 | 0.28 | 0.28 | 0.05 | 0.02 | 2.21 | 0.26 | 0.24 | 0.39 | 0.02 | 0.29 | 0.06 | 3.07 | 2.7 | 0 | 0.3 | 0 | 0 | 0
School | 0.13699 | 0.057078 | 445106 | 7.46 | 0.13 | 1.17 | 0.96 | 0.5 | 0.1 | 0.18 | 2.88 | 0.74 | 0.46 | 0.25 | 0 | 0.08 | 0.01 | 15.97 | 10 | 0.1 | 4.7 | 1.1 | 0 | 0.1
College | 0.2968 | 0.052511 | 205942 | 12.26 | 0.77 | 1.91 | 2.05 | 0.46 | 0.12 | 0.27 | 3.84 | 0.91 | 0.72 | 0.49 | 0.01 | 0.58 | 0.14 | 34.24 | 19.8 | 3.5 | 8.4 | 1.7 | 0.9 | 0
Health | 1.1301 | 0.08105 | 232606 | 19.61 | 0.71 | 3.87 | 4.04 | 0.71 | 0.08 | 0.43 | 4.81 | 0.57 | 0.86 | 2.52 | 0.01 | 0.78 | 0.22 | 75.53 | 32.7 | 1.6 | 31.4 | 3.4 | 1.4 | 5.1
Lodging | 0.69635 | 0.10274 | 270044 | 12.13 | 0.42 | 2.41 | 1.79 | 0.9 | 0.03 | 0.68 | 3.5 | 0.61 | 0.17 | 1.11 | 0 | 0.48 | 0.02 | 42.4 | 7.3 | 0.1 | 29 | 4.4 | 1.4 | 0.3
Miscellaneous | 0.75342 | 0.098174 | 1099544 | 9.84 | 0.09 | 1.1 | 0.86 | 0.86 | 0.13 | 0.26 | 2.61 | 1.07 | 0.35 | 1 | 0.12 | 1.08 | 0.3 | 23.34 | 7 | 0.4 | 9.3 | 1 | 1 | 4.6
All Offices | 0.12557 | 0.053653 | 1022012 | 16.08 | 0.38 | 3.23 | 2.43 | 0.47 | 0.17 | 0.11 | 4.24 | 0.65 | 3.09 | 0.65 | 0.02 | 0.54 | 0.09 | 17.9 | 14.2 | 0.4 | 2.3 | 0.2 | 0.1 | 0.8
All Warehouses | 0.068493 | 0.25228 | 649706 | 6.74 | 0.03 | 0.33 | 0.28 | 2.21 | 0.04 | 0.02 | 2.29 | 0.27 | 0.23 | 0.42 | 0.02 | 0.52 | 0.08 | 3.44 | 2.4 | 0 | 0.4 | 0.2 | 0 | 0.4
Food Preparation | 35.0685 | 2.2534
Assembly | 0.022831 | 0.06621
No default | n.a. | n.a.
Use whole building data | n.a. | n.a.
Note on A18: Charles Eley: This is added with double the values for restaurant. The assumption is that the food preparation area is half the size of the restaurant.
Note on A19: Charles Eley: The values for small office are used for this added category.

## ECB-CS (hidden)
|  | (ft²/person) | (W/ft2) | (Btu/h-person) | (CFM/ft²) | [CFM/person] |  | (W/ft² | Reference to Compliance Supplement
|  | Occupant Density | Receptacle Power | Service Water Heating | Minimum O.A. | Minimum O.A. | Operating Schedule (Table 7.1.C) | Lighting Power Density |  | Building Type | Space Function
Building Type | BA Assembly | 50 | 0.25 | 215 | 0.3 | 15 | I | 2.07 | BA | Assembly
| BA Educational | 75 | 0.5 | 215 | 0.2 | 15 | D | 1.29 | BA | Educational
| BA Food Service | 100 | 0.1 | 390 | 0.25 | 25 | B | 1.37 | BA | Food Service
| BA Health & Institutional | 200 | 1 | 135 | 0.4 | 80 | H | 1.44 | BA | Health & Institutional
| BA Industrial | 750 | 0.2 | 225 | 0.45 | 340 | C | 1.21 | BA | Industrial
| BA Lodging | 250 | 0.25 | 1700 | 0.05 | 30 | F | 1.15 | BA | Lodging
| BA N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BA | N/A
| BA Office (Business) | 250 | 0.75 | 300 | 0.08 | 20 | A | 1.26 | BA | Office (Business)
| BA Retail | 300 | 0.25 | 135 | 0.2 | 60 | C | 2.48 | BA | Retail
| BA Warehouse (Storage) | 15000 | 0.1 | 1000 | 0.2 | 750 | E | 1.03 | BA | Warehouse (Storage)
Common Space Types | CS Active storage | 500 | 0 | 0 | 0.04 | 15 | * | 1.19 | CS | Active storage
| CS Atria- 1st three floors | 100 | 0.25 | 0 | 0.1 | 10 | * | 1.36 | CS | Atria- 1st three floors
| CS Auto repair | 200 | 0.5 | 300 | 1.5 | 300 | C | 1.31 | CS | Auto repair
| CS Banking activity | 200 | 0.75 | 300 | 0.1 | 20 | A | 2.33+ | CS | Banking activity
| CS Classroom/lecture/training | 75 | 0.5 | 215 | 0.2 | 15 | * | 1.45 | CS | Classroom/lecture/training
| CS Conf./mtg./multi-use | 50 | 0.1 | 150 | 0.4 | 20 | * | 0.92 | CS | Conf./mtg./multi-use
| CS Corridor/transition | 1000 | 0 | 0 | 0.05 | 50 | * | 0.57 | CS | Corridor/transition
| CS Dining area- General | 100 | 0.1 | 300 | 0.2 | 20 | * | 1.31 | CS | Dining area- General
| CS Dressing/locker/fitting | 100 | 0.25 | 0 | 0.5 | 50 | * | 0.91 | CS | Dressing/locker/fitting
| CS Food preparation | 200 | 1 | 400 | 0.3 | 60 | * | 1.19 | CS | Food preparation
| CS Inactive storage | 1000 | 0 | 0 | 0.04 | 15 | * | 0.81 | CS | Inactive storage
| CS Ironing/sorting | 200 | 2 | 215 | 0.1 | 20 | * | 1.28 | CS | Ironing/sorting
| CS Laboratory/research | 200 | 1 | 600 | 0.1 | 20 | A | 1.64+ | CS | Laboratory/research
| CS Lobby | 100 | 0.25 | 100 | 0.15 | 15 | * | 1.77 | CS | Lobby
| CS Lounge/recreation | 100 | 0.1 | 300 | 0.2 | 20 | * | 1.32 | CS | Lounge/recreation
| CS Mechanical/electrical | 2000 | 0.1 | 0 | 0.05 | 100 | * | 0.81 | CS | Mechanical/electrical
| CS Office - enclosed | 200 | 0.75 | 300 | 0.1 | 20 | A | 1.49 | CS | Office - enclosed
| CS Office - open | 200 | 0.75 | 300 | 0.1 | 20 | A | 1.24 | CS | Office - open
| CS Reception/waiting | 100 | 0.25 | 100 | 0.15 | 15 | * | 1.52 | CS | Reception/waiting
| CS Restrooms | 300 | 0.1 | 0 | 0.167 | 50 | * | 0.77 | CS | Restrooms
| CS Stairs- active | 1000 | 0 | 0 | 0.05 | 50 | * | 0.81 | CS | Stairs- active
| CS Stairs- inactive | 5000 | 0 | 0 | 0.05 | 250 | * | 0.58 | CS | Stairs- inactive
| CS Washing | 200 | 2 | 215 | 0.125 | 25 | * | 1.28 | CS | Washing
Space Function | SS Civil Services Courtroom | 75 | 0.25 | 100 | 0.2 | 15 | A | 1.98 | SS | Civil Services | Courtroom
| SS Civil Services Fire engine room | 250 | 0.25 | 1110 | 0.08 | 20 | H | 0.83 | SS | Civil Services | Fire engine room
| SS Civil Services Jail/peniten. living area | 250 | 0.25 | 1110 | 0.08 | 20 | H | 0.96 | SS | Civil Services | Jail/peniten. living area
| SS Civil Services Police laboratory | 200 | 1 | 600 | 0.15 | 30 | H | 1.64 | SS | Civil Services | Police laboratory
| SS Civil Services Post office sorting areas | 200 | 0.75 | 300 | 0.1 | 20 | A | 0.78 | SS | Civil Services | Post office sorting areas
| SS Education Classroom | 75 | 0.5 | 215 | 0.2 | 15 | D | 1.45 | SS | Education | Classroom
| SS Education Dressing/lockers | 100 | 0.25 | 0 | 0.5 | 50 | G | 0.91 | SS | Education | Dressing/lockers
| SS Education Laboratory | 100 | 0.5 | 600 | 0.2 | 20 | D | 1.64 | SS | Education | Laboratory
| SS Education Study hall | 250 | 0.25 | 300 | 0.06 | 15 | G | 1.45 | SS | Education | Study hall
| SS Exhibition Hall Exhibit space | 50 | 0.25 | 100 | 0.3 | 15 | C | 0.96+ | SS | Exhibition Hall | Exhibit space
| SS Food Bar/lounge | 100 | 0.1 | 300 | 0.3 | 30 | B | 1.85 | SS | Food | Bar/lounge
| SS Food Cafeteria/fast food | 100 | 0.1 | 400 | 0.2 | 20 | B | 1.31 | SS | Food | Cafeteria/fast food
| SS Food Family dining | 100 | 0.1 | 300 | 0.2 | 20 | B | 1.85 | SS | Food | Family dining
| SS Food Leisure dining | 100 | 0.1 | 300 | 0.2 | 20 | B | 1.85 | SS | Food | Leisure dining
| SS Garage Parking garage | Uncond. |  |  |  |  | H | 0.26 | SS | Garage | Parking garage
| SS General Dormitory | 250 | 0.25 | 1700 | 0.06 | 15 | G | 1.73 | SS | General | Dormitory
| SS General Guest rooms | 250 | 0.25 | 2000 | 0.12 | 30 | F | 1.46 | SS | General | Guest rooms
| SS General Recep./waiting/prefunc. | 100 | 0.25 | 200 | 0.15 | 15 | C | 0.89 | SS | General | Recep./waiting/prefunc.
| SS Health Corridors- Health | 100 | 0.1 | 0 | 0.2 | 20 | H | 0.92 | SS | Health | Corridors- Health
| SS Health Examination | 200 | 1 | 300 | 0.075 | 15 | C | 2.47 | SS | Health | Examination
| SS Health Laboratory | 200 | 1 | 600 | 0.15 | 30 | H | 3.19 | SS | Health | Laboratory
| SS Health Medical supplies | 200 | 0.1 | 0 | 0.15 | 30 | H | 2.41 | SS | Health | Medical supplies
| SS Health Nurse station/Pharmacy | 200 | 0.25 | 150 | 0.075 | 15 | H | 2.09 | SS | Health | Nurse station/Pharmacy
| SS Health Patient rooms/nursery | 200 | 1 | 300 | 0.125 | 25 | H | 1.34 | SS | Health | Patient rooms/nursery
| SS Health Reception/waiting | 100 | 0.1 | 0 | 0.2 | 20 | H | 1.09 | SS | Health | Reception/waiting
| SS Health Recovery | 200 | 1 | 600 | 0.075 | 15 | H | 2.41 | SS | Health | Recovery
| SS Health Surgery/emergency/OB | 200 | 1 | 1000 | 0.15 | 30 | H | 3.19 | SS | Health | Surgery/emergency/OB
| SS Health Therapy | 200 | 1 | 150 | 0.125 | 25 | C | 2.09 | SS | Health | Therapy
| SS Hotels Banquet | 100 | 0.1 | 300 | 0.15 | 15 | B | 2.09 | SS | Hotels | Banquet
| SS Hotels Dining- Hotel | 100 | 0.25 | 300 | 0.15 | 14 | B | 2.09 | SS | Hotels | Dining- Hotel
| SS Hotels Lobby-Hotel | 100 | 0.25 | 100 | 0.15 | 15 | H | 1.27 | SS | Hotels | Lobby-Hotel
| SS Library Card file/cataloging | 200 | 0.25 | 300 | 0.075 | 15 | C | 1.42+ | SS | Library | Card file/cataloging
| SS Library Reading area | 200 | 0.25 | 300 | 0.075 | 15 | C | 1.67 | SS | Library | Reading area
| SS Library Stacks | 200 | 0.25 | 300 | 0.075 | 15 | C | 1.78 | SS | Library | Stacks
| SS Manufacture Control room | 17500 | 0 | 1000 | 0.05 | 875 | C | 1.97 | SS | Manufacture | Control room
| SS Manufacture Electronic/detail | 300 | 1 | 175 | 0.25 | 75 | C | 2.92 | SS | Manufacture | Electronic/detail
| SS Manufacture Equipment room | 17500 | 0 | 1000 | 0.05 | 875 | C | 0.87 | SS | Manufacture | Equipment room
| SS Manufacture General manufacturing | 300 | 1 | 175 | 0.25 | 75 | C | 2.66 | SS | Manufacture | General manufacturing
| SS Manufacture General workshop | 300 | 1 | 175 | 0.5 | 150 | C | 2.83 | SS | Manufacture | General workshop
| SS Manufacture Painting/welding | 300 | 1 | 300 | 1 | 300 | C | 2.66 | SS | Manufacture | Painting/welding
| SS Motels Dining- Motel | 100 | 0.25 | 300 | 0.15 | 15 | B | 1.85 | SS | Motels | Dining- Motel
| SS Motels Lobby- Motel | 100 | 0.25 | 100 | 0.15 | 15 | H | 1.77 | SS | Motels | Lobby- Motel
| SS Museum General exhibition | 50 | 0.25 | 215 | 0.3 | 15 | C | 1.03 | SS | Museum | General exhibition
| SS Museum Restoration | 200 | 0.5 | 175 | 0.1 | 20 | A | 2.14 | SS | Museum | Restoration
| SS Museum Storage (artifacts)- active | 1000 | 0.1 | 225 | 0.05 | 50 | E | 0.81 | SS | Museum | Storage (artifacts)- active
| SS Museum Storage (artifacts)- inactive | 10000 | 0 | 225 | 0.05 | 500 | E | 1.19 | SS | Museum | Storage (artifacts)- inactive
| SS Religious Worship- congregation | 50 | 0.1 | 50 | 0.3 | 15 | I | 3.68+ | SS | Religious | Worship- congregation
| SS Religious Worship- pulpit, choir | 50 | 0.1 | 50 | 0.3 | 15 | I | 5.46 | SS | Religious | Worship- pulpit, choir
| SS Retail Department store | 300 | 0.25 | 135 | 0.2 | 60 | C | 3.53 | SS | Retail | Department store
| SS Retail Dressing/fitting rooms | 300 | 0 | 135 | 0.05 | 15 | C | 2.55 | SS | Retail | Dressing/fitting rooms
| SS Retail Fine merchandise | 300 | 0.25 | 135 | 0.2 | 60 | C | 5.68 | SS | Retail | Fine merchandise
| SS Retail Mall concourse | 200 | 0 | 215 | 0.1 | 20 | C | 1.74 | SS | Retail | Mall concourse
| SS Retail Mass merchandising | 300 | 0.25 | 135 | 0.2 | 60 | C | 1.23 | SS | Retail | Mass merchandising
| SS Retail Personal services | 300 | 0.25 | 135 | 0.2 | 60 | C | 1.28 | SS | Retail | Personal services
| SS Retail Specialty store | 300 | 0.25 | 135 | 0.2 | 60 | C | 2.68 | SS | Retail | Specialty store
| SS Retail Supermarket | 300 | 0.25 | 135 | 0.2 | 60 | C | 2.25 | SS | Retail | Supermarket
| SS Sports Boxing/wrestling ring | 50 | 0.15 | 200 | 0.4 | 20 | I | 7.51 | SS | Sports | Boxing/wrestling ring
| SS Sports Boxing/wrestling ring | 50 | 0.1 | 300 | 0.4 | 20 | I | 3.76 | SS | Sports | Boxing/wrestling ring
| SS Sports Exercise area | 50 | 0.1 | 300 | 0.4 | 20 | I | 1.13 | SS | Sports | Exercise area
| SS Sports Gymnasium playing area | 50 | 0.1 | 300 | 0.4 | 20 | I | 1.88 | SS | Sports | Gymnasium playing area
| SS Sports Indoor athletics seating | 50 | 0 | 100 | 0.3 | 15 | I | 0.3 | SS | Sports | Indoor athletics seating
| SS Sports Jai-alai/tennis/hockey | 50 | 0.15 | 200 | 0.4 | 20 | I | 5.32 | SS | Sports | Jai-alai/tennis/hockey
| SS Sports Locker room/shower | 100 | 0.25 | 0 | 0.5 | 50 | I | 0.91 | SS | Sports | Locker room/shower
| SS Sports Other/televised play. area | 50 | 0.15 | 200 | 0.4 | 20 | I | 3.76 | SS | Sports | Other/televised play. area
| SS Theater Auditorium seating area | 50 | 0.25 | 100 | 0.3 | 15 | C | 1.62 | SS | Theater | Auditorium seating area
| SS Theater Dressing rooms | 100 | 0.25 | 0 | 0.5 | 50 | * | 2.55 | SS | Theater | Dressing rooms
| SS Theater Lobby - other theaters | 100 | 0.1 | 0 | 0.2 | 20 | C | 0.78 | SS | Theater | Lobby - other theaters
| SS Theater Lobby - Performing Arts | 100 | 0.1 | 0 | 0.2 | 20 | C | 1.99 | SS | Theater | Lobby - Performing Arts
| SS Theater Motion picture seating | 50 | 0.25 | 100 | 0.3 | 15 | I | 1.02 | SS | Theater | Motion picture seating
| SS Theater Performing arts seating | 75 | 0.25 | 100 | 0.2 | 15 | I | 2 | SS | Theater | Performing arts seating
| SS Transport Terminal- baggage | 200 | 0.25 | 215 | 0.1 | 20 | H | 0.77 | SS | Transport | Terminal- baggage
| SS Transport Terminal- concourse | 200 | 0 | 215 | 0.1 | 20 | H | 0.67+ | SS | Transport | Terminal- concourse
| SS Transport Terminal- dining area | 100 | 0.1 | 300 | 0.2 | 20 | H | 1.85 | SS | Transport | Terminal- dining area
| SS Transport Terminal- ticket counter | 100 | 0.25 | 215 | 0.2 | 20 | H | 1.61 | SS | Transport | Terminal- ticket counter
| SS Transport Terminal- waiting/lounge | 100 | 0 | 215 | 0.2 | 20 | H | 0.9 | SS | Transport | Terminal- waiting/lounge
| SS Warehouse Fine material | 500 | 0.1 | 225 | 0.05 | 25 | E | 1.72 | SS | Warehouse | Fine material
| SS Warehouse Inactive stor./elec/mech | 17500 | 0 | 1000 | 0.05 | 875 | E | 1.19 | SS | Warehouse | Inactive stor./elec/mech
| SS Warehouse Medium/Bulky material | 1000 | 0.1 | 225 | 0.05 | 50 | E | 1.19 | SS | Warehouse | Medium/Bulky material
| No default | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a.
| Use whole building data | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a.

## ACM05 (hidden)
|  | Whole Building Notes |  | Note 1 | Note 2 | Note 2 | Note 3 |  | Note 4 | Note 5
|  | Sub-Occupancy Notes |  | Note 2 | Note 3 | Note 3 | Note 4 |  | Note 5 | Note 5
|  |  |  | Person/1000 ft² | Btu/person | Btu/person | W/ft² | Btu/h-person | W/ft² | cfm/ft²
| Cl | Table Name | Lookup Name | Occupant Density | Sensible Heat Gain Per Person | Latent Heat Gain per Person | Receptacle Load | Hot Water Load | Lighting Power | Ventilation Rate
Whole Building (Building Area) | BA | Other | BA Other | 10 | 250 | 200 | 1 | 120 | 0.6 | 0.15 | Note 8
| BA | Auditoriums | BA Auditoriums | 143 | 245 | 105 | 1 | 60 | 1.5 | 1.07
| BA | Classroom Building | BA Classroom Building | 40 | 246 | 171 | 1 | 108 | 1.1 | 0.32
| BA | Commercial and Industrial Building | BA Commercial and Industrial Building | 5 | 268 | 403 | 0.43 | 108 | 0.6 | 0.15
| BA | Convention Centers | BA Convention Centers | 136 | 245 | 112 | 0.96 | 57 | 1.2 | 1.02 | Note 8
| BA | Financial Institutions | BA Financial Institutions | 10 | 250 | 250 | 1.5 | 120 | 1.1 | 0.15
| BA | General Commercial and Industrial Work Buildings, High Bay | BA General Commercial and Industrial Work Buildings, High Bay | 7 | 375 | 625 | 1 | 120 | 1 | 0.15
| BA | General Commercial and Industrial Work Buildings, Low Bay | BA General Commercial and Industrial Work Buildings, Low Bay | 7 | 375 | 625 | 1 | 120 | 1 | 0.15
| BA | Grocery Stores | BA Grocery Stores | 29 | 252 | 225 | 0.91 | 113 | 1.5 | 0.22 | Note 8
| BA | Library | BA Library | 10 | 250 | 250 | 1.5 | 120 | 1.3 | 0.15
| BA | Medical Buildings and Clinics | BA Medical Buildings and Clinics | 10 | 250 | 213 | 1.18 | 110 | 1.1 | 0.15
| BA | Office Buildings | BA Office Buildings | 10 | 250 | 206 | 1.34 | 106 | 0.85 | 0.15
| BA | Religious Facilities | BA Religious Facilities | 136 | 245 | 112 | 0.96 | 57 | 1.6 | 1.03 | Note 8
| BA | Restaurants | BA Restaurants | 45 | 274 | 334 | 0.79 | 366 | 1.2 | 0.38 | Note 8
| BA | Schools | BA Schools | 40 | 246 | 171 | 1 | 108 | 1 | 0.32 | Note 8
| BA | Theaters | BA Theaters | 130 | 268 | 403 | 0.54 | 60 | 1.3 | 0.98 | Note 8
Sub-Occupancy Type (Note 1) | SO | Auditorium | SO Auditorium | 143 | 245 | 105 | 1 | 60 | 1.5 | 1.07 | Note 10
| SO | Auto Repair | SO Auto Repair | 10 | 275 | 475 | 1 | 120 | 0.9[i] | 1.5
| SO | Bar, Cocktail Lounge and Casino | SO Bar, Cocktail Lounge and Casino | 67 | 275 | 275 | 1 | 120 | 1.1 | 0.5 | Note 10
| SO | Beauty Salon | SO Beauty Salon | 10 | 250 | 200 | 2 | 120 | 1.7 | 0.4
| SO | Classrooms, Lecture, Training, Vocational Room | SO Classrooms, Lecture, Training, Vocational Room | 50 | 245 | 155 | 1 | 120 | 1.2 | 0.38
| SO | Civic Meeting Place | SO Civic Meeting Place | 25 | 250 | 200 | 1.5 | 120 | 1.3 | 0.19 | Note 10
| SO | Commercial and Industrial Storage (conditioned or unconditioned) | SO Commercial and Industrial Storage (conditioned or unconditioned) | 3 | 275 | 475 | 0.2 | 120 | 0.6 | 0.15
| SO | Commercial and Industrial Storage (refrigerated) | SO Commercial and Industrial Storage (refrigerated) | 1 | 275 | 475 | 0.2 | 0 | 0.7 | 0.15
| SO | Convention, Conference, Multi-purpose and Meeting Centers (Note 10) | SO Convention, Conference, Multi-purpose and Meeting Centers (Note 10) | 67 | 245 | 155 | 1 | 60 | 1.4 | 0.5
| SO | Corridors, Restrooms, Stairs, and Support Areas | SO Corridors, Restrooms, Stairs, and Support Areas | 10 | 250 | 250 | 0.2 | 0 | 0.6 | 0.15
| SO | Dining | SO Dining | 67 | 275 | 275 | 0.5 | 385 | 1.1 | 0.5 | Note 10
| SO | Electrical, Mechanical Room | SO Electrical, Mechanical Room | 3 | 250 | 250 | 0.2 | 0 | 0.7 | 0.15
| SO | Exercise, Center, Gymnasium | SO Exercise, Center, Gymnasium | 20 | 255 | 875 | 0.5 | 120 | 1 | 0.15
| SO | Exhibit, Museum | SO Exhibit, Museum | 67 | 250 | 250 | 1.5 | 60 | 2 | 0.5 | Note 10
| SO | Financial Transaction | SO Financial Transaction | 10 | 250 | 250 | 1.5 | 120 | 1.2 | 0.15
| SO | Dry Cleaning (Coin Operated) | SO Dry Cleaning (Coin Operated) | 10 | 250 | 250 | 3 | 120 | 0.9 | 0.3
| SO | Dry Cleaning (Full Service Commercial) | SO Dry Cleaning (Full Service Commercial) | 10 | 250 | 250 | 3 | 120 | 0.9 | 0.45
| SO | General Commercial and Industrial Work, High Bay | SO General Commercial and Industrial Work, High Bay | 10 | 275 | 475 | 1 | 120 | 1. 0 | 0.15
| SO | General Commercial and Industrial Work, Low Bay | SO General Commercial and Industrial Work, Low Bay | 10 | 275 | 475 | 1 | 120 | 0.9 | 0.15
| SO | General Commercial and Industrial Work, Precision | SO General Commercial and Industrial Work, Precision | 10 | 250 | 200 | 1 | 120 | 1. 2 | 0.15
| SO | Grocery Sales | SO Grocery Sales | 33 | 250 | 200 | 1 | 120 | 1.6 | 0.25 | Note 10
| SO | High-Rise Residential Living Spaces | SO High-Rise Residential Living Spaces | 5 | 245 | 155 | 0.5 | 1700 | 0.5 | 0.15 | Note 9
| SO | Hotel Function Area | SO Hotel Function Area | 67 | 250 | 200 | 0.5 | 60 | 1.5 | 0.5 | Note 10
| SO | Hotel/Motel Guest Room | SO Hotel/Motel Guest Room | 5 | 245 | 155 | 0.5 | 2800 | 0.5 | 0.15 | Note 9
| SO | Housing, Public and Common Areas: Multi-family, Dormitory | SO Housing, Public and Common Areas: Multi-family, Dormitory | 10 | 250 | 250 | 0.5 | 120 | 1 | 0.15
| SO | Housing, Public and Common Areas:, Senior Housing | SO Housing, Public and Common Areas:, Senior Housing | 10 | 250 | 250 | 0.5 | 120 | 1.5 | 0.15
| SO | Kitchen, Food Preparation | SO Kitchen, Food Preparation | 5 | 275 | 475 | 1.5 | 385 | 1.6 | 0.15
| SO | Laboratory, Scientific | SO Laboratory, Scientific | 10 | 250 | 200 | 1 | 120 | 1.4 | 0.38
| SO | Laundry | SO Laundry | 10 | 250 | 250 | 3 | 385 | 0.9 | 0.15
| SO | Library, Reading Areas | SO Library, Reading Areas | 20 | 250 | 200 | 1.5 | 120 | 1.2 | 0.15
| SO | Library, Stacks | SO Library, Stacks | 10 | 250 | 200 | 1.5 | 120 | 1.5 | 0.15
| SO | Lobby, Hotel | SO Lobby, Hotel | 10 | 250 | 250 | 0.5 | 120 | 1.1 | 0.15
| SO | Lobby, Main Entry | SO Lobby, Main Entry | 10 | 250 | 250 | 0.5 | 60 | 1.5 | 0.15
| SO | Locker/Dressing Room | SO Locker/Dressing Room | 20 | 255 | 475 | 0.5 | 385 | 0.8 | 0.15
| SO | Lounge, Recreation | SO Lounge, Recreation | 67 | 275 | 275 | 1 | 60 | 1.1 | 0.5 | Note 10
| SO | Malls and Atria | SO Malls and Atria | 33 | 250 | 250 | 0.5 | 120 | 1.2 | 0.25 | Note 10
| SO | Medical and Clinical Care | SO Medical and Clinical Care | 10 | 250 | 200 | 1.5 | 160 | 1.2 | 0.15
| SO | Office (Greater than 250 square feet in floor area) | SO Office (Greater than 250 square feet in floor area) | 10 | 250 | 200 | 1.5 | 120 | 0.9 | 0.15
| SO | Office (250 square feet in floor area or less) | SO Office (250 square feet in floor area or less) | 10 | 250 | 200 | 1.5 | 120 | 1.1 | 0.15
| SO | Police Station and Fire Station | SO Police Station and Fire Station | 10 | 250 | 200 | 1.5 | 120 | 0.9 | 0.15
| SO | Religious Worship | SO Religious Worship | 143 | 245 | 105 | 0.5 | 60 | 1.5 | 1.07 | Note 10
| SO | Retail Merchandise Sales, Wholesale Showroom | SO Retail Merchandise Sales, Wholesale Showroom | 33 | 250 | 200 | 1 | 120 | 1.6 | 0.25 | Note 10
| SO | Tenant Lease Space | SO Tenant Lease Space | 10 | 250 | 200 | 1.5 | 120 | 1 | 0.15
| SO | Theater, Motion Picture | SO Theater, Motion Picture | 143 | 245 | 105 | 0.5 | 60 | 0.9 | 1.07 | Note 10
| SO | Theater, Performance | SO Theater, Performance | 143 | 245 | 105 | 0.5 | 60 | 1.4 | 1.07 | Note 10
| SO | Transportation Function | SO Transportation Function | 33 | 250 | 250 | 0.5 | 120 | 1.2 | 0.25 | Note 10
| SO | Waiting Area | SO Waiting Area | 10 | 250 | 250 | 0.5 | 120 | 1.1 | 0.15
| SO | All Others | SO All Others | 10 | 250 | 200 | 1 | 120 | 0.6 | 0.15
|  |  | No default | n.a. | n.a. | n.a. | n.a. | n.a. | n.a. | n.a.
|  |  | Use whole building data | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD | UWBD
Notes for Whole Building Table
(1) Most occupancy values are based on an assumed mix of sub-occupancies within the area. These values were based on one half the maximum occupant load for exiting purposes in the CBC. Full value for design conditions. Full year operational schedules reduce these values by up to 50% for compliance simulations and full year test simulations.
(2) From Table 1, p. 29.4, ASHRAE 2001Handbook of Fundamentals
(3) From Lawrence Berkeley Laboratory study. This value is fixed and includes all equipment that is plugged into receptacle outlets.
(4) From Table 146-E of the Standards for the applicable occupancy. The lighting power density of the standard building, for areas where no lighting plans or specifications are submitted for permit and the occupancy of the building is not known, is 1.2 watts per square foot.
(5) Developed from § 121 and Table 121-A of the Standards
(6) Hotel uses values for Hotel Function Area from Table N2-6.
(7) For retail and wholesale stores, the complete building method may only be used when the sales area is 70% or greater of the building area.
(8) For these occupancies, when the proposed design is required to have demand control ventilation by § 121 (c) 3 the ventilation rate is the minimum that would occur at any time during occupied hours. Additional ventilation would be provided through demand controlled ventilation to maintain CO2 levels according to § 121 of the Standards.
Notes for Space by Space Table
(1) Subcategories of these sub-occupancies are described in Section 2.4.1.1 (Occupancy Types) of this manual.
(2) Values based on one half the maximum occupant load for exiting purposes in the CBC. Full value for design conditions. Full year operational schedules reduce these values by up to 50% for compliance simulations and full year test simulations.
(3) From Table 1, p. 29.4, ASHRAE 2001 Handbook of Fundamentals.
(4) From Lawrence Berkeley Laboratory study. This value is fixed and includes all equipment that is plugged into receptacle outlets.
(5) From Table 146-F of the Standards for the applicable occupancy. Compliance software shall use this value for the standard building design when lighting compliance is performed for the zone or area in question.
(6) Developed from 121 and Table 121-A of the Standards.
(7) Refer to residential water heating method.
(8) The use of this occupancy category is an exceptional condition that shall appear on the exceptional conditions checklist and thus requires special justification and documentation and independent verification by the local enforcement agency.
(9) For hotel/motel guest rooms and high-rise residential living spaces all these values are fixed and are the same for both the proposed design and the standard design. Compliance software shall ignore user inputs that modify these assumptions for these two occupancies. Spaces in high-rise residential buildings other than living spaces shall use the values for Housing, Public and Common Areas (either multi-family or senior housing).
(10) For these occupancies, when the proposed design is required to have demand control ventilation by § 121 (c) 3 the ventilation rate is the minimum that would occur at any time during occupied hours. Additional ventilation would be provided through demand controlled ventilation to maintain CO2 levels according to § 121.
(11) From Benya, July 2006 Workshop, Changes to Lighting Power Density Values: Bringing Certain Values in Line with Standard 90.1, http://www.energy.ca.gov/title24/2008standards/documents/2006-07-12_workshop/MEASURE_BLD_02.PDF
Note on I42: Charles Eley: Note that this value was previously "-7" which was clearly wrong. This value is taken from ECB-CS for dormitories.

## NREL41956 (not used) (hidden)
|  |  |  | Service Hot Water (Note 1) | [5 empty] | Default Outside Air Rate (Note 2) |  | From Kristin
PBA Code | Lookup Name | PBA Name | Sub Name | Use Rate (l/d-occ) | Storage Value (l/occ) | Recovery Rate (ml/occ) | Use Rate (gal/d-occ) | Storage Value (gal/occ) | Recovery Rate (gal/h-occ) | l/s-occ | cfm/occ | Default OA Rate (cfm/occ) | SHW (L/occ-d)
1 | Vacant | Vacant |  | 0 | 6 | 0.2 | 0 | 1.585 | 0.88058 | 0 | 0 | 0 | 0
2 | Office/Professional < 30,000 ft² | Office/Professional | < 30,000 ft² | 3.8 | 6 | 0.2 | 1.0039 | 1.585 | 0.88058 | 26.1 | 55.3083 | 55.3/45.3 (7) | 3.8
2 | Office/Professional > 30,000 ft² | Office/Professional | > 30,000 ft² | 3.8 | 6 | 0.2 | 1.0039 | 1.585 | 0.88058 | 21.4 | 45.3486 | 55.3/45.3 (7) | 3.8
4 | Laboratory | Laboratory |  | 38 | 30 | 2 | 10.0386 | 7.9252 | 8.8058 | 18.7 | 39.627 | 39.6 | 38
5 | Nonrefrigerated warehouse | Nonrefrigerated warehouse |  | 2.3 | 6 | 0.2 | 0.6076 | 1.585 | 0.88058 | 5 | 10.5955 | 10.6 | 2.3
6 | Food sales | Food sales |  | 19 | 30 | 1 | 5.0193 | 7.9252 | 4.4029 | 18.7 | 39.627 | 39.6 | 19
7 | Public order and safety | Public order and safety |  | 3.8 | 6 | 0.2 | 1.0039 | 1.585 | 0.88058 | 18.7 | 39.627 | 39.6 | 3.8
8 | Outpatient health care | Outpatient health care |  | 11.4 | 18 | 0.6 | 3.0116 | 4.7551 | 2.6417 | 18.7 | 39.627 | 39.6 | 11.4
11 | Refrigerated warehouse | Refrigerated warehouse |  | 2.3 | 5 | 0.2 | 0.6076 | 1.3209 | 0.88058 | 2 | 4.2382 | 4.2 | 2.3
12 | Religious worship | Religious worship |  | 1 | 2 | 0.1 | 0.26417 | 0.52835 | 0.44029 | 18.7 | 39.627 | 39.6 | 1
13 | Public assembly | Public assembly |  | 1 | 2 | 0.1 | 0.26417 | 0.52835 | 0.44029 | 18.7 | 39.627 | 39.6 | 1
14 | Education college | Education | college | 2.3 | 6 | 0.2 | 0.6076 | 1.585 | 0.88058 | 6.3 | 13.3503 | 13.4 | 2.3/6.8 (2)
14 | Education elementary | Education | elementary | 2.3 | 6 | 0.2 | 0.6076 | 1.585 | 0.88058 | 6.3 | 13.3503
14 | Education high school | Education | high school | 6.8 | 12 | 0.4 | 1.7964 | 3.1701 | 1.7612 | 6.3 | 13.3503
14 | Education pre-school | Education | pre-school | 2.3 | 6 | 0.2 | 0.6076 | 1.585 | 0.88058 | 6.3 | 13.3503
15 | Food service | Food service |  | 38 | 60 | 2 | 10.0386 | 15.8504 | 8.8058 | 18.7 | 39.627 | 39.6 | 38
16 | Inpatient health care | Inpatient health care |  | 11.4 | 18 | 0.6 | 3.0116 | 4.7551 | 2.6417 | 18.7 | 39.627 | 39.6 | 11.4
17 | Skilled nursing | Skilled nursing |  | 11.4 | 18 | 0.6 | 3.0116 | 4.7551 | 2.6417 | 18.7 | 39.627 | 39.6 | 11.4
25 | Retail | Retail |  | 2.3 | 4 | 0.2 | 0.6076 | 1.0567 | 0.88058 | 18.7 | 39.627 | 39.6 | 2.3
26 | Service | Service |  | 3.8 | 6 | 0.2 | 1.0039 | 1.585 | 0.88058 | 18.7 | 39.627 | 39.6 | 3.8
91 | Other | Other |  | 3.8 | 6 | 0.2 | 1.0039 | 1.585 | 0.88058 | 18.7 | 39.627 | 39.6 | 3.8
| (do not select) | (do not select) |  | l/d-rm |  |  | gal/d-rm
18 | Lodging < 20 rooms | Lodging | < 20 rooms | 75.8 | 50 | 3 | 20.0243 | 13.2086 | 13.2086 | 18.7 | 39.627 | 39.6 | 75.8/53.1/37.9 (5)
18 | Lodging 20-100 rooms | Lodging | 20-100 rooms | 53.1 | 50 | 3 | 14.0276 | 13.2086 | 13.2086 | 18.7 | 39.627 | 39.6 | 75.8/53.1/37.9 (5)
18 | Lodging >100 rooms | Lodging | >100 rooms | 37.9 | 50 | 3 | 10.0122 | 13.2086 | 13.2086 | 18.7 | 39.627 | 39.6 | 75.8/53.1/37.9 (5)
Notes
1 |  | Source is Table C40, NREL TP-550-41956
2 |  | Source is Table C39, NREL TP-550-41956
Conversions
|  | litres per gallon | 3.7854
|  | l/s per cfm | 0.4719
|  | ml/s per gal/h | 0.22712
Notes
[5 empty] | 1 | The hot water load for hotels, motels, dormitories, and penetentiaries is 20
gallons/day-occupant for facilities with 20 or fewer rooms; 14 gallong/day-occupant for
facilities with 20 to 100 rooms; and 10 gallons/day-occupant for facilities with more than
100 rooms.
[5 empty] | 2 | The hot water load for dwellling units shall be calculated as 30 gallons/day per dwelling
unit plus 10 gallons/day per bedroom. Efficiency apartments shall be consdered to have
zero bedrooms.
[5 empty] | 3 | The hot water load for schools shall be 1.8 gallons/day-occupant for high schools and
0.6 gallons/day-occupant for other schools.
[5 empty] | N/A | No default is provided.

## Process and Plug (not used) (hidden)
(COMNET Plug Load )PBA Plus EPD |  | Csd | Pdmisc(W/m2) | Pdmisc(W/ft2) | DF |  | Refrigeration Power Density (W/ft2) | Mean Power Density (w/ft2) | Mean Power Density (Btu/h-ft2) | Standard Deviation W/ft2
Vacant | 0.59733 | 2 | 5.9 | 0.54807 | 1 | Vacant | 0 | 0 | 0 | 0
Administrative/professional office | 2.0196 | 2 | 8.3 | 0.77102 | 1 | Office/professional < 30,000 ft2 | 0.07 | 0.04 | 0.13648 | 0.002
Bank/other financial | 2.2548 | 2 | 8.3 | 0.77102 | 1 | Office/professional > 30,000 ft 2 | 0.06 | 0.04 | 0.13648 | 0.002
Government office | 2.1354 | 2 | 8.3 | 0.77102 | 1 | Laboratory | 0.28 | 3.72 | 12.6926 | 0.248
Medical office (non-diagnostic) | 1.7177 | 2 | 8.3 | 0.77102 | 1 | Nonrefrigerated warehouse | 0.05 | 0 | 0 | 0
Mixed-use office | 2.1912 | 2 | 8.3 | 0.77102 | 1 | Food sales | 2.6 | 0.35 | 1.1942 | 0.023
Other office | 2.8203 | 2 | 8.3 | 0.77102 | 1 | Public order and safety | 0.06 | 0.09 | 0.30708 | 0.006
Laboratory | 3.7328 | 2 | 30 | 2.7868 | 1 | Outpatient health care | 0.08 | 0.33 | 1.126 | 0.022
Distribution/shipping center | 0.3875 | 2 | 2 | 0.18579 | 1 | Refrigerated warehouse | 1.53 | 0.13 | 0.44356 | 0.009
Non-refrigerated warehouse | 0.34576 | 2 | 2 | 0.18579 | 1 | Religious worship | 0.03 | 0.04 | 0.13648 | 0.002
Self-storage | 0.24214 | 2 | 2 | 0.18579 | 1 | Public assembly | 0.03 | 0.04 | 0.13648 | 0.002
Convenience store | 1.1155 | 2 | 5.1 | 0.47376 | 1 | Education (not incl. University) | 0.06 | 0.04 | 0.13648 | 0.003
Convenience store with gas station | 0.99476 | 2 | 5.1 | 0.47376 | 1 | Food service | 1.12 | 5.14 | 17.5377 | 0.342
Grocery store/food market | 0.7821 | 2 | 5.1 | 0.47376 | 1 | Inpatient health care | 0.08 | 0.33 | 1.126 | 0.022
Other food sales | 0.67325 | 2 | 5.1 | 0.47376 | 1 | Skilled nursing | 0.08 | 0.33 | 1.126 | 0.022
Fire station/police station | 1.5772 | 2 | 12 | 1.1147 | 1 | Lodging | 0.14 | 0.2 | 0.6824 | 0.014
Other public order and safety | 1.6041 | 2 | 12 | 1.1147 | 1 | Retail (except malls) | 0.15 | 0.03 | 0.10236 | 0.002
Medical office (diagnostic) | 1.7987 | 2 | 5.9 | 0.54807 | 1 | Service (except food) | 0.12 | 0.22 | 0.75064 | 0.015
Clinic/other outpatient health | 1.3276 | 2 | 5.9 | 0.54807 | 1 | Other | 0.1 | 0.09 | 0.30708 | 0.006
Refrigerated warehouse | 0.16933 | 2 | 1 | 0.092894 | 1
Religious worship | 0.31384 | 2 | 5.9 | 0.54807 | 0.4
Entertainment/culture | 0.7303 | 2 | 5.9 | 0.54807 | 1
Library | 1.1041 | 2 | 5.9 | 0.54807 | 1
Recreation | 0.70972 | 2 | 5.9 | 0.54807 | 1
Social/meeting | 0.71806 | 2 | 5.9 | 0.54807 | 1
Other public assembly | 0.82509 | 2 | 5.9 | 0.54807 | 1
College/university | 1.4877 | 1.6 | 8 | 0.74315 | 1
Elementary/middle school | 0.86616 | 2 | 1.6 | 0.14863 | 1
High school | 0.77829 | 2 | 1.6 | 0.14863 | 1
Preschool/daycare | 0.52419 | 2 | 1.6 | 0.14863 | 1
Other classroom education | 0.90505 | 2 | 2 | 0.18579 | 1
Fast food | 1.4926 | 2 | 10 | 0.92894 | 1
Restaurant/cafeteria | 1.2161 | 2 | 10 | 0.92894 | 1
Other food service | 1.3078 | 2 | 10 | 0.92894 | 1
Hospital/inpatient health | 1.6837 | 2 | 8.2 | 0.76173 | 1
Nursing home/assisted living | 1.4288 | 2 | 12 | 1.1147 | 1
Dormitory/fraternity/sorority | 1.5767 | 2 | 3.2 | 0.29726 | 1
Hotel | 0.77582 | 2 | 3.2 | 0.29726 | 1
Motel or inn | 0.70721 | 2 | 3.2 | 0.29726 | 1
Other lodging | 0.67301 | 2 | 3.2 | 0.29726 | 1
Vehicle dealership/showroom | 0.87779 | 2 | 3.7 | 0.34371 | 1
Retail store | 0.51832 | 2 | 3.7 | 0.34371 | 1
Other retail | 0.69522 | 2 | 3.7 | 0.34371 | 1
Post office/postal center | 1.5046 | 2 | 5.9 | 0.54807 | 1
Repair shop | 0.57158 | 2 | 5.9 | 0.54807 | 1
Vehicle service/repair shop | 0.6393 | 2 | 5.9 | 0.54807 | 1
Vehicle storage/maintenance | 0.34368 | 2 | 5.9 | 0.54807 | 1
Other service | 0.47727 | 2 | 5.9 | 0.54807 | 1
Other | 2.6792 | 2 | 5.9 | 0.54807 | 1
Strip shopping mall | 0
Enclosed mall | 0

## bEQ (hidden)
|  | 1 - Lighting |  |  |  | 2 - Plug Loads |  |  |  |  | 3 - Occupancy |  |  |  | 4 - Outdoor Air |  | 5 - Water Heating |  | 6 - Process |  | 7 - Schedules
|  | Allowed Lighting Power Density (W/ft²) |  |  |  | Default Receptacle Power Density (W/ft²) |  | Receptacle Power Coefficients |  |  | Occupant Density (ft³/person) |  | Heat Gain per Occupant (Btu/occ) |  | Minimum Ventilation (cfm/ft²) |  | Load (Btu/h-occ) |  | Interior Gas Appliance Power Density (Btu/h-ft²) | Refrigeration Power Density (W/ft²)
|  | ASHRAE Standard 90.1-2001 | ASHRAE Standard 90.1-2007 | ASHRAE Standard 90.1-2010 | Room Cavity Ratio Threshold | California 2005 ACM | COMNET | Csd | PDmisc | D | California 2005 ACM | COMNET | Sensible | Latent | California 2005 ACM | COMNET | California 2005 ACM | COMNET |  |  | California 2005 Schedule | COMNET Schedule
Mapping to NREL-956 | Whole Building Categories
Education PBA | School/University | 1.5 | 1.2 | 0.99 | n.a. | 1 | 0.68748 | 2 | 0.1487 | 1 | 25 | 75 | 246 | 171 | 0.32 | 0.32 | 108 | 215 | 0.13699 | 0.057078 | Non-Residential | Table G-M School Occupancy
Food service Fast food | Dining, Cafeteria/Fast Food | 1.8 | 1.4 | 0.9 | n.a. | 0.79 | 1.3684 | 2 | 0.92937 | 1 | 22.2222 | 100 | 274 | 334 | 0.38 | 0.38 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | Table G-K Restaurant Occupancy
Food service Other food service | Dining, Bar/Cocktail Lounge | 1.5 | 1.3 | 0.99 | n.a. | 0.79 | 1.3161 | 2 | 0.92937 | 1 | 22.2222 | 100 | 274 | 334 | 0.38 | 0.38 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | Table G-K Restaurant Occupancy
Food service Restaurant/cafeteria | Dining, Family | 1.9 | 1.6 | 0.89 | n.a. | 0.79 | 1.263 | 2 | 0.92937 | 1 | 22.2222 | 100 | 274 | 334 | 0.38 | 0.38 | 366 | 390 | 17.5342 | 1.1267 | Non-Residential | Table G-K Restaurant Occupancy
Inpatient health care PBA | Hospital | 1.6 | 1.2 | 1.21 | n.a. | 1.18 | 1.2488 | 2 | 0.76208 | 1 | 100 | 200 | 250 | 213 | 0.15 | 0.15 | 110 | 135 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Lodging Dormitory/fraternity/sorority | Dormitory | 1.5 | 1 | 0.61 | n.a. | 0.5 | 1.9561 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 0.15 | N/A | 2800 | 1700 | 0.69635 | 0.10274 | Residential | Table G-G Hotel/Motel Occupancy
Lodging Hotel | Hotel | 1.7 | 1 | 1 | n.a. | 0.5 | 1.5641 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 0.15 | N/A | 2800 | 1700 | 0.69635 | 0.10274 | Hotel Function | Table G-G Hotel/Motel Occupancy
Lodging Hotel | Motel | 2 | 1 | 0.88 | n.a. | 0.5 | 1.5641 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 0.15 | N/A | 2800 | 1700 | 0.69635 | 0.10274 | Residential | Table G-G Hotel/Motel Occupancy
Lodging Other lodging | Multi-Family | 1 | 0.7 | 0.6 | n.a. | 0.5 | 1.4245 | 2 | 0.2974 | 1 | 200 | 250 | 245 | 155 | 0.15 | 0.15 | 1700 | 1700 | 0.69635 | 0.10274 | Residential | Table G-G Hotel/Motel Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing Facility | 2.2 | 1.3 | 1.11 | n.a. | 1 | 0.34481 | 2 | 0.18587 | 1 | 142.8571 | 750 | 375 | 625 | 0.15 | 0.15 | 120 | 225 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse Non-refrigerated warehouse | Warehouse | 1.2 | 0.8 | 0.66 | n.a. | 0.2 | 0.30231 | 2 | 0.18587 | 1 | 333.3333 | 15000 | 275 | 475 | 0.15 | 0.15 | 120 | 1000 | 0 | 0.031963 | Non-Residential | Table G-N Warehouse Occupancy
Office Government office | Court House | 1.4 | 1.2 | 1.05 | n.a. | 0.96 | 1.669 | 2 | 0.77138 | 1 | 7.3529 | 200 | 245 | 112 | 1.02 | 1.07 | 57 | 135 | 0.17123 | 0.046804 | Non-Residential | Table G-E Assembly Occupancy
Office PBA | Office | 1.3 | 1 | 0.9 | n.a. | 1.34 | 1.6721 | 2 | 0.77138 | 1 | 100 | 250 | 250 | 206 | 0.15 | 0.15 | 106 | 300 | 0.12557 | 0.053653 | Non-Residential | Table G-I Office Occupancy
Outpatient health care PBA | Health Care Clinic | 1.6 | 1 | 0.87 | n.a. | 1.18 | 1.2202 | 2 | 0.54833 | 1 | 100 | 200 | 250 | 213 | 0.15 | 0.15 | 110 | 135 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Public assembly Entertainment/culture | Motion Picture Theatre | 1.6 | 1.2 | 0.83 | n.a. | 1 | 0.74485 | 2 | 0.54833 | 1 | 6.993 | 50 | 245 | 105 | 1.07 | 0.98 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Entertainment/culture | Museum- General | 1.6 | 1.1 | 1.06 | n.a. | 1.5 | 0.74485 | 2 | 0.54833 | 1 | 14.9254 | 50 | 250 | 250 | 0.5 | 0.15 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Entertainment/culture | Performing Arts Theatre | 1.5 | 1.6 | 1.36 | n.a. | 0.5 | 0.74485 | 2 | 0.54833 | 1 | 6.993 | 50 | 245 | 105 | 1.07 | 0.98 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Library | Library | 1.5 | 1.3 | 1.18 | n.a. | 1.5 | 0.93723 | 2 | 0.54833 | 1 | 100 | 75 | 250 | 250 | 0.15 | 0.15 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Convention Center | 1.4 | 1.2 | 1.08 | n.a. | 0.96 | 0.74761 | 2 | 0.54833 | 1 | 7.3529 | 50 | 245 | 112 | 1.02 | 1.02 | 57 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Sports Arena | 1.5 | 1.1 | 0.78 | n.a. | 1 | 0.74761 | 2 | 0.54833 | 1 | 6.993 | 50 | 245 | 105 | 1.07 | 1.07 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Town Hall | 1.4 | 1.1 | 0.92 | n.a. | 1.34 | 0.74761 | 2 | 0.54833 | 1 | 100 | 50 | 250 | 206 | 0.15 | 1.07 | 106 | 215 | 0.12557 | 0.053653 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Exercise Center | 1.4 | 1 | 0.88 | n.a. | 1 | 0.67425 | 2 | 0.54833 | 1 | 100 | 200 | 250 | 200 | 0.15 | 0.15 | 120 | 135 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Gymnasium | 1.7 | 1.1 | 1 | n.a. | 0.5 | 0.67425 | 2 | 0.54833 | 1 | 50 | 200 | 255 | 875 | 0.15 | 0.15 | 120 | 135 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public order and safety Fire station/police station | Fire Station | 1.3 | 1 | 0.71 | n.a. | 1.5 | 1.5404 | 2 | 1.1152 | 1 | 100 | 250 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | Table G-I Office Occupancy
Public order and safety Fire station/police station | Police Station | 1.3 | 1 | 0.96 | n.a. | 1.5 | 1.5404 | 2 | 1.1152 | 1 | 100 | 250 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | Table G-I Office Occupancy
Public order and safety Other public order and safety | Penitentiary | 1.2 | 1 | 0.97 | n.a. | 0.5 | 1.4928 | 2 | 1.1152 | 1 | 200 | 250 | 245 | 155 | 0.15 | 0.15 | 2800 | 1700 | 0.69635 | 0.10274 | Residential | Table G-E Assembly Occupancy
Religious worship PBA | Religious Building | 2.2 | 1.3 | 1.05 | n.a. | 0.96 | 0.29845 | 2 | 0.54833 | 0.4 | 7.3529 | 50 | 245 | 112 | 1.03 | 1.03 | 57 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Retail (except Malls) PBA | Retail | 1.9 | 1.5 | 1.4 | n.a. | 1 | 0.70235 | 2 | 0.34387 | 1 | 30.303 | 300 | 250 | 200 | 0.25 | N/A | 120 | 135 | 0.091324 | 0.11758 | Retail | Table G-L Retail Occupancy
Service (except Food) Other service | Transportation | 1.2 | 1 | 0.77 | n.a. | 0.5 | 0.51912 | 2 | 0.54833 | 1 | 30.303 | 200 | 250 | 250 | 0.25 | 0.15 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Service (except Food) Post office/postal center | Post Office | 1.6 | 1.1 | 0.87 | n.a. | 1 | 0.90907 | 2 | 0.54833 | 1 | 100 | 250 | 275 | 475 | 0.15 | 0.15 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | Table G-I Office Occupancy
Service (except Food) Repair shop | Workshop | 1.7 | 1.4 | 1.2 | n.a. | 1 | 0.42834 | 2 | 0.54833 | 1 | 142.8571 | 750 | 375 | 625 | 0.15 | 0.15 | 120 | 225 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Service (except Food) Vehicle service/repair shop | Auto Repair | 1.5 | 0.9 | 0.82 | n.a. | 1 | 0.50325 | 2 | 0.54833 | 1 | 100 | 200 | 275 | 475 | 1.5 | 1.5 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Service (except Food) Vehicle storage/maintenance | Parking Garage | 0.3 | 0.3 | 0.25 | n.a. | 1 | n.a. | n.a. | n.a. | n.a. | 100 | Uncond. | 250 | 200 | 0.15 | 0.15 | 120 | 0 | 0 | 0.031963 | Retail | Table G-J Parking Garage Occupancy
Mapping to NREL-956 | Space-by-Space Classifications
Education Other classroom education | Classroom/Lecture/Training | 1.6 | 1.4 | 1.24 | 4 | 1 | 0.58913 | 2 | 0.18587 | 1 | 20 | 20 | 245 | 155 | 0.38 | 0.38 | 120 | 215 | 0.13699 | 0.057078 | Non-Residential | Table G-M School Occupancy
Education Other classroom education | Penitentiary Classroom | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | 20 | 20 | 245 | 155 | 0.38 | 0.38 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-M School Occupancy
Food service Other food service | Dining Area, Family Dining | 2.2 | 2.1 | 0.89 | 4 | 0.2 | 1.3161 | 2 | 0.92937 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 0 | 300 | 17.5342 | 1.1267 | Non-Residential | Table G-K Restaurant Occupancy
Food service Other food service | Food Preparation | 2.2 | 1.2 | 0.99 | 6 | 1.5 | 1.3161 | 2 | 0.92937 | 1 | 200 | 200 | 275 | 475 | 0.15 | 0.15 | 385 | 400 | 35.0685 | 2.2534 | Non-Residential | Table G-K Restaurant Occupancy
Food service Restaurant/cafeteria | Dining Area, General | 1.4 | 0.9 | 0.65 | 4 | 0.5 | 1.3161 | 2 | 0.92937 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 385 | 300 | 17.5342 | 1.1267 | Non-Residential | Table G-K Restaurant Occupancy
Food service Restaurant/cafeteria | Dining Area, Bar Lounge/Leisure Dining | 1.2 | 1.4 | 1.31 | 4 | 1 | 1.263 | 2 | 0.92937 | 1 | 15 | 30 | 275 | 275 | 0.5 | 0.5 | 120 | 300 | 17.5342 | 1.1267 | Non-Residential | Table G-K Restaurant Occupancy
Food service Restaurant/cafeteria | Hotel Dining | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 15 | 30 | 275 | 275 | 0.5 | 0.5 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-K Restaurant Occupancy
Food service Restaurant/cafeteria | Highway Lodging Dining | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 15 | 30 | 275 | 275 | 0.5 | 0.5 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-K Restaurant Occupancy
Food service Restaurant/cafeteria | Penitentiary Dining | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 15 | 15 | 275 | 275 | 0.5 | 0.5 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-K Restaurant Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Corridor/Transition | 1.6 | 1 | 0.89 | Width < 8 ft | 0.2 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Emergency | 2.8 | 2.7 | 2.26 | 6 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 1000 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Exam/Treatment | 1.6 | 1.5 | 1.66 | 8 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Laundry/Washing | #REF! | #REF! | #REF! | #REF! | 3 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 250 | 250 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Lounge/Recreation | 1.4 | 0.8 | 1.07 | 6 | 0.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 0 | 0.022831 | 0.06621 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Medical Supply | 3 | 1.4 | 1.27 | 6 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 0 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Nursery | 1 | 0.6 | 0.88 | 6 | 0.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Nurses’ Station | 1.8 | 1 | 0.87 | 6 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 150 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Operating Room | 7.6 | 2.2 | 1.89 | 6 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 1000 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Patient Room | 1.2 | 0.7 | 0.62 | 6 | 0.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 300 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Pharmacy | #REF! | #REF! | #REF! | #REF! | 1.5 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 250 | 200 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Physical Therapy | 1.9 | 0.9 | 0.91 | 6 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 150 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Radiology/Imaging | #REF! | #REF! | #REF! | #REF! | 1.5 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 250 | 200 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-F Health Occupancy
Inpatient health care Hospital/inpatient health | Hospital, Recovery | 2.6 | 0.8 | 1.15 | 6 | 1.5 | 1.2488 | 2 | 0.76208 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 160 | 600 | 1.1301 | 0.08105 | Non-Residential | Table G-F Health Occupancy
Laboratory PBA | Laboratory, Classrooms | 1.6 | 1.4 | 1.28 | 6 | 1 | 3.3415 | 2 | 2.7881 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 215 | 0.2968 | 0.052511 | Residential | Table G-G Hotel/Motel Occupancy
Laboratory PBA | Laboratory, Medical/Industrial/Research | 1.8 | 1.4 | 1.81 | 6 | 1 | 3.3415 | 2 | 2.7881 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 600 | n.a. | n.a. | Residential | Table G-G Hotel/Motel Occupancy
Lodging Dormitory/fraternity/sorority | Dormitory, Living Quarters | 1.9 | 1.1 | 0.38 | 8 | 0.5 | 1.9561 | 2 | 0.2974 | 1 | 100 | 150 | 250 | 250 | 0.15 | 0.15 | 120 | 1700 | 0.69635 | 0.10274 | Residential | Table G-G Hotel/Motel Occupancy
Lodging Hotel | Hotel Guest Rooms | 2.5 | 1.1 | 1.11 | 6 | 0.5 | 1.5641 | 2 | 0.2974 | 1 | 200 | 200 | 245 | 155 | 0.15 | 0.15 | 2800 | 2000 | 0.69635 | 0.10274 | Residential | Table G-G Hotel/Motel Occupancy
Lodging Motel or inn | Highway Lodging Guest Rooms | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 200 | 200 | 245 | 155 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-G Hotel/Motel Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing, Corridor/Transition | 0.5 | 0.5 | 0.41 | Width < 8 ft | 0.2 | 0.34481 | 2 | 0.18587 | 1 | 100 | 200 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0.022831 | 0.06621 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing, Detailed Manufacturing | 6.2 | 2.1 | 1.29 | 4 | 1 | 0.34481 | 2 | 0.18587 | 1 | 100 | 200 | 250 | 200 | 0.15 | 0.15 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing, Equipment Room | 0.8 | 1.2 | 0.95 | 6 | 0.2 | 0.34481 | 2 | 0.18587 | 1 | 333 | 750 | 250 | 250 | 0.15 | 0.15 | 120 | 1000 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing, Extra High Bay (>50 ft Floor to Ceiling Height) | 3 | 1.7 | 1.05 | 4 | 1 | 0.34481 | 2 | 0.18587 | 1 | 100 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing, High Bay (25–50 ft Floor to Ceiling Height) | 3 | 1.7 | 1.23 | 4 | 1 | 0.34481 | 2 | 0.18587 | 1 | 100 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse Distribution/shipping center | Manufacturing, Low Bay (<25 ft Floor to Ceiling Height) | 2.1 | 1.2 | 1.19 | 4 | 1 | 0.34481 | 2 | 0.18587 | 1 | 100 | 200 | 275 | 475 | 0.15 | 0.15 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Nonrefrigerated warehouse PBA | Storage, Active, Musuem | #REF! | #REF! | #REF! | #REF! | 0.2 | #REF! | #REF! | #REF! | #REF! | 333 | 333 | 275 | 475 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-N Warehouse Occupancy
Nonrefrigerated warehouse PBA | Storage, Inactive, Musuem | #REF! | #REF! | #REF! | #REF! | 0.2 | #REF! | #REF! | #REF! | #REF! | 333 | 333 | 275 | 475 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-N Warehouse Occupancy
Nonrefrigerated warehouse PBA | Storage, Inactive, General | 0.3 | 0.3 | 0.63 | 6 | 0.2 | 0.31395 | 2 | 0.18587 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 0 | 0 | 0.031963 | Non-Residential | Table G-N Warehouse Occupancy
Nonrefrigerated warehouse PBA | Storage | 1.1 | 0.8 | 0.63 | 6 | 0.2 | 0.31395 | 2 | 0.18587 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 0 | 0 | 0.031963 | Non-Residential | Table G-N Warehouse Occupancy
Nonrefrigerated warehouse PBA | Warehouse, Fine Material Storage | 1.6 | 1.4 | 0.95 | 6 | 0.2 | 0.31395 | 2 | 0.18587 | 1 | 333 | 333 | 275 | 475 | 0.15 | 0.15 | 120 | 225 | 0 | 0.031963 | Non-Residential | Table G-N Warehouse Occupancy
Nonrefrigerated warehouse PBA | Warehouse, Medium/Bulky Material Storage | 1.1 | 0.9 | 0.58 | 4 | 0.5 | 0.31395 | 2 | 0.18587 | 1 | 30 | 30 | 250 | 250 | 0.25 | 0.25 | 120 | 225 | 0 | 0.031963 | Non-Residential | Table G-E Assembly Occupancy
Nursing Nursing home/assisted living | Home Nursing/Senior Housing | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 100 | 200 | 250 | 250 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Residential | Table G-G Hotel/Motel Occupancy
Office Bank/other financial | Bank/Office,Banking Activity Area | 2.4 | 1.5 | 1.38 | 6 | 1.5 | 1.7201 | 2 | 0.77138 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | Table G-I Office Occupancy
Office PBA | Mechanical Control Room | #REF! | #REF! | #REF! | #REF! | 0.2 | #REF! | #REF! | #REF! | #REF! | 333 | 750 | 250 | 250 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-H Light Manufacturing Occupancy
Office PBA | Office, Enclosed | 1.5 | 1.1 | 1.11 | 8 | 1.5 | 1.6721 | 2 | 0.77138 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | Table G-I Office Occupancy
Office PBA | Office, Open Plan | 1.3 | 1.1 | 0.98 | 4 | 1.5 | 1.6721 | 2 | 0.77138 | 1 | 100 | 150 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.12557 | 0.053653 | Non-Residential | Table G-I Office Occupancy
Other PBA | Atrium,(First 40 ft in height) | 1.3 | 0.6 | 0.03 (watts per ft height) | n.a. |  | n.a. | n.a. | n.a. | n.a. | [6 empty] | 120 | 0 | 0.022831 | 0.06621
Other PBA | Atrium,(Height above 40 ft ) | 0.2 | 0.2 | 0.02 (watts per ft height) | n.a. |  | n.a. | n.a. | n.a. | n.a. | [6 empty] | 120 | 0 | 0.022831 | 0.06621
Other PBA | Corridor/Transition | 0.7 | 0.5 | 0.66 | Width<8 ft | 0.2 | UWBD | UWBD | UWBD | UWBD | 100 | 200 | 250 | 250 | 0.15 | 0.15 | 0 | 0 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Other PBA | Locker Room | 0.8 | 0.6 | 0.75 | 6 | 0.5 | n.a. | n.a. | n.a. | n.a. | 50 | 50 | 255 | 475 | 0.15 | 0.15 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | Table G-E Assembly Occupancy
Other PBA | Restrooms | 1 | 0.9 | 0.98 | 8 | 0.5 | UWBD | UWBD | UWBD | UWBD | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 0 | 0 | n.a. | n.a. | Non-Residential | Table G-E Assembly Occupancy
Other PBA | Retail Dressing/Fitting Room | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 50 | 50 | 255 | 475 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-L Retail Occupancy
Other PBA | Stairway | 0.9 | 0.6 | 0.69 | 10 | 1 | UWBD | UWBD | UWBD | UWBD | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 0 | 0 | n.a. | n.a. | Non-Residential | Table G-E Assembly Occupancy
Public assembly Entertainment/culture | Lobby, Motion Picture Theater | 0.8 | 1.1 | 2 | 6 | 0.5 | 0.74485 | 2 | 0.54833 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | 0 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Entertainment/culture | Lobby, Performing Arts Theater | 1.2 | 3.3 | 0.52 | 4 | 0.5 | 0.74485 | 2 | 0.54833 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | 0 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Entertainment/culture | Museum, General Exhibition | 1.6 | 1 | 1.05 | 6 | 0.2 | 0.74485 | 2 | 0.54833 | 1 | 333 | 200 | 275 | 475 | 0.15 | 0.15 | 60 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Library | Library, Card File and Cataloging | #REF! | #REF! | #REF! | #REF! | 1.5 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 250 | 200 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Library | Library, Reading Area | 1.8 | 1.2 | 0.93 | 4 | 1.5 | 0.93723 | 2 | 0.54833 | 1 | 50 | 50 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Library | Library, Stacks | 1.9 | 1.7 | 1.71 | 4 | 1.5 | 0.93723 | 2 | 0.54833 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Hotel Lobby | 1.7 | 1.1 | 1.06 | 4 | 0.5 | 1.5641 | 2 | 0.2974 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 100 | 0.022831 | 0.06621 | Residential | Table G-G Hotel/Motel Occupancy
Public assembly Other public assembly | Lobby, General | 1.8 | 1.3 | 0.9 | 4 | 0.5 | UWBD | UWBD | UWBD | UWBD | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Lobby, Elevator | 1.8 | 1.3 | 0.64 | 6 | 0.5 | UWBD | UWBD | UWBD | UWBD | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Penitentiary Audience Seating | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | 7 | 9 | 245 | 105 | 1.07 | 1.07 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Sports Arena, Audience Seating | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | 7 | 9 | 245 | 105 | 1.07 | 1.07 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Transportation, Air/Train/Bus—Baggage Area | 1.3 | 1 | 0.76 | 4 | 0.5 | 0.76225 | 2 | 0.54833 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Transportation, Airport—Concourse | 0.7 | 0.6 | 0.36 | 4 | 0.5 | 0.76225 | 2 | 0.54833 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Transportation, Audience Seating | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 30 | 60 | 250 | 250 | 0.25 | 0.25 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Other public assembly | Transportation, Terminal—Ticket Counter | 1.8 | 1.5 | 1.08 | 4 | 0.5 | 0.76225 | 2 | 0.54833 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 215 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Audience/Seating Area, Permanent for Auditorium | 1.6 | 0.9 | 0.79 | 6 | 1 | 0.74761 | 2 | 0.54833 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Audience/Seating Area, Permanent for Motion Picture Theater | 0.5 | 0.7 | 0.82 | 4 | 1 | 0.74761 | 2 | 0.54833 | 1 | 333 | 5000 | 275 | 475 | 0.15 | 0.15 | 60 | 150 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Audience/Seating Area, Permanent for Performing Arts Theater | 0.5 | 0.3 | 0.43 | 6 | 1 | 0.67425 | 2 | 0.54833 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 120 | 100 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Convention Center, Audience Seating | 0.8 | 1.2 | 0.95 | 6 | 1 | n.a. | n.a. | n.a. | n.a. | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 120 | n.a. | n.a. | n.a. | Non-Residential | Table G-E Assembly Occupancy
Public assembly PBA | Convention Center, Exhibit Space | 3.3 | 1.3 | 1.45 | 4 | 1 | 0.74761 | 2 | 0.54833 | 1 | 15 | 30 | 245 | 155 | 0.15 | 0.15 | 60 | 100 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Gymnasium/Fitness Center, Fitness Area | 1.1 | 0.9 | 0.72 | 4 | 0.5 | 0.67425 | 2 | 0.54833 | 1 | 50 | 50 | 255 | 875 | 0.15 | 0.15 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Gymnasium/Fitness Center, Gymnasium Audience Seating | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 50 | 50 | 255 | 875 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Gymnasium/Fitness Center, Playing Area | 1.9 | 1.4 | 1.2 | 4 | 0.5 | 0.67425 | 2 | 0.54833 | 1 | 50 | 50 | 255 | 875 | 0.15 | 0.15 | 120 | 300 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Lounge/Recreation | 1.4 | 1.2 | 0.73 | 4 | 1 | UWBD | UWBD | UWBD | UWBD | 15 | 100 | 275 | 275 | 0.5 | 0.5 | 60 | 300 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Sports Arena, Court Sports Arena—Class 1 | 4.3 | 2.3 | 0.72 | 4 | 1 | 0.67425 | 2 | 0.54833 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 300 | 0.022831 | 0.06621 | Retail | Table G-E Assembly Occupancy
Public assembly Recreation | Sports Arena, Court Sports Arena—Class 2 | 4.3 | 2.3 | 1.2 | 4 | 1 | 0.67425 | 2 | 0.54833 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 200 | 0.022831 | 0.06621 | Retail | Table G-E Assembly Occupancy
Public assembly Recreation | Sports Arena, Court Sports Arena—Class 3 | 4.3 | 2.3 | 1.92 | 4 | 1 | 0.67425 | 2 | 0.54833 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 200 | 0.022831 | 0.06621 | Retail | Table G-E Assembly Occupancy
Public assembly Recreation | Sports Arena, Court Sports Arena—Class 4 | 4.3 | 2.3 | 3.01 | 4 | 1 | 0.67425 | 2 | 0.54833 | 1 | 30 | 100 | 250 | 200 | 0.25 | 0.25 | 120 | 200 | 0.022831 | 0.06621 | Retail | Table G-E Assembly Occupancy
Public assembly Recreation | Sports Arena, Indoor Sports Fields | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | 7 | 9 | 245 | 105 | 1.07 | 1.07 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Recreation | Sports Arena, Ring Sports Arena | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | 7 | 9 | 245 | 105 | 1.07 | 1.07 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Public assembly Social/meeting | Conference/Meeting/Multipurpose | 1.5 | 1.3 | 1.23 | 6 | 1 | 0.73324 | 2 | 0.54833 | 1 | 15 | 15 | 245 | 155 | 0.5 | 0.5 | 60 | 150 | 0.2968 | 0.052511 | Non-Residential | Table G-E Assembly Occupancy
Public order and safety Fire station/police station | Fire Stations, Engine Room | #REF! | #REF! | #REF! | #REF! | 1.5 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 250 | 200 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-I Office Occupancy
Public order and safety Fire station/police station | Fire Stations, Sleeping Quarters | 1.1 | 0.3 | 0.25 | 6 | 0.5 | 1.5404 | 2 | 1.1152 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 1700 | 0.69635 | 0.10274 | Residential | Table G-I Office Occupancy
Public order and safety Other public order and safety | Courthouse/Police Station/Penitentiary, Confinement Cells | 1.1 | 0.9 | 1.1 | 6 | 0.2 | 1.4928 | 2 | 1.1152 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 120 | 1110 | 0.69635 | 0.10274 | Residential | Table G-E Assembly Occupancy
Public order and safety Other public order and safety | Courthouse/Police Station/Penitentiary, Courtroom | 2.1 | 1.9 | 1.72 | 6 | 1.5 | 1.4928 | 2 | 1.1152 | 1 | 40 | 40 | 250 | 200 | 0.19 | 0.19 | 120 | 100 | 0.17123 | 0.046804 | Non-Residential | Table G-E Assembly Occupancy
Public order and safety Other public order and safety | Courthouse/Police Station/Penitentiary, Judges’ Chambers | 1.1 | 1.3 | 1.17 | 8 | 1.5 | 1.4928 | 2 | 1.1152 | 1 | 100 | 100 | 250 | 200 | 0.15 | 0.15 | 120 | 300 | 0.17123 | 0.046804 | Non-Residential | Table G-E Assembly Occupancy
Refrigerated warehouse PBA | Warehouse, Refrigerated | #REF! | #REF! | #REF! | #REF! | 0.2 | #REF! | #REF! | #REF! | #REF! | 333 | 333 | 275 | 475 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-N Warehouse Occupancy
Religious worship PBA | Religious Buildings, Audience Seating | #REF! | #REF! | #REF! | #REF! | 0.5 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 275 | 475 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-E Assembly Occupancy
Religious worship PBA | Religious Buildings, Fellowship Hall | 2.3 | 0.9 | 0.64 | 4 | 0.5 | 0.29845 | 2 | 0.54833 | 0.4 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 60 | 50 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Religious worship PBA | Religious Buildings, Worship Pulpit, Choir | 5.2 | 2.4 | 1.53 | 4 | 1 | 0.29845 | 2 | 0.54833 | 0.4 | 100 | 100 | 275 | 475 | 1.07 | 1.07 | 60 | 50 | 0.022831 | 0.06621 | Non-Residential | Table G-E Assembly Occupancy
Retail (except Malls) Other retail | Dressing/Fitting Room , Performing Arts Theater | 0.8 | 0.6 | 0.4 | 6 | 0.5 | 0.82157 | 2 | 0.34387 | 1 | 7 | 9 | 245 | 105 | 1.07 | 1.07 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | Table G-E Assembly Occupancy
Retail (except Malls) Other retail | Retail Mall Concourse | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF! | 30 | 60 | 250 | 200 | 0.25 | 0.25 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-L Retail Occupancy
Retail (except Malls) Retail store | Retail Sales Area | 2.1 | 1.7 | 1.68 | 6 | 0.5 | 0.54928 | 2 | 0.34387 | 1 | 30 | 60 | 250 | 250 | 0.25 | 0.25 | 120 | 135 | 0.091324 | 0.11758 | Retail | Table G-L Retail Occupancy
Service (except Food) Other service | Laundry Facility | 0.7 | 0.6 | 0.6 | 4 | 3 | 0.51912 | 2 | 0.54833 | 1 | 100 | 100 | 250 | 250 | 0.15 | 0.15 | 385 | 215 | n.a. | n.a. | Residential | Table G-G Hotel/Motel Occupancy
Service (except Food) Post office/postal center | Post Office, Sorting Area | #REF! | #REF! | #REF! | #REF! | 0.2 | #REF! | #REF! | #REF! | #REF! | 100 | 100 | 250 | 250 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-I Office Occupancy
Service (except Food) Repair shop | Museum, Restoration | 2.5 | 1.7 | 1.02 | 6 | 1.5 | 0.42834 | 2 | 0.54833 | 1 | 15 | 30 | 250 | 250 | 0.5 | 0.5 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | Table G-E Assembly Occupancy
Service (except Food) Repair shop | Workshop, General | 2.5 | 1.9 | 1.59 | 6 | 0.2 | 0.42834 | 2 | 0.54833 | 1 | 1000 | 500 | 275 | 475 | 0.15 | 0.15 | 120 | 175 | 0.75342 | 0.098174 | Non-Residential | Table G-N Warehouse Occupancy
Service (except Food) Vehicle service/repair shop | Automotive,Service/Repair | 1.4 | 0.7 | 0.67 | 4 | 1 | 0.50325 | 2 | 0.54833 | 1 | 100 | 100 | 275 | 475 | 1.5 | 1.5 | 120 | 300 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Service (except Food) Vehicle storage/maintenance | Parking Garage, Garage Area | 0.2 | 0.2 | 0.19 | 4 | 1.5 | n.a. | n.a. | n.a. | n.a. | 100 | N/A | 250 | 250 | 0.15 | 0.15 | 120 | 0 | 0 | 0.031963 | Non-Residential | Table G-J Parking Garage Occupancy
Vacant PBA | Electrical/Mechanical | 1.3 | 1.5 | 0.95 | 6 | 0.2 | 0.57608 | 2 | 0.54833 | 1 | 333 | 750 | 250 | 250 | 0.15 | 0.15 | 120 | 0 | 0.75342 | 0.098174 | Non-Residential | Table G-H Light Manufacturing Occupancy
Vacant PBA | Equipment Room | #REF! | #REF! | #REF! | #REF! | 0.2 | #REF! | #REF! | #REF! | #REF! | 333 | 750 | 250 | 250 | 0.15 | 0.15 | #REF! | #REF! | #REF! | #REF! | Non-Residential | Table G-H Light Manufacturing Occupancy
Note on T2: Source: CEUS
Note on U2: Source: CEUS
Note on C3: Source: 90.1-2001
Note on D3: Source: 90.1-2007
Note on E3: Source: 90.1-2010
Note on F3: Source: 90.1-2010
Note on G3: Source: ACM05
Note on H3: Source: NREL956
Note on I3: Source: NREL956
Note on J3: Source: NREL956
Note on K3: Source: NREL956
Note on L3: Source: ACM05
Note on M3: Source: ECB-CS
Note on N3: Source: 90.1-2001
Note on O3: Source: 90.1-2001
Note on P3: Source: ACM05
Note on Q3: Source: ACM05
Note on R3: Source: ACM05
Note on S3: Source: ECB-CS

## Pivots (hidden)
| PBA Plus Laboratory | 3
Mapping to NREL41956 | Mapping to 90.1-2010 | Brandemuehl Comments
Service (except Food) Vehicle service/repair shop | BA Automotive Facility
Public assembly PBA | BA Convention Center
Office Government office | BA Courthouse | 2
Food service Other food service | BA Dining: Bar Lounge/Leisure
Food service Fast food | BA Dining: Cafeteria/Fast Food
Food service Restaurant/cafeteria | BA Dining: Family
Lodging Dormitory/fraternity/sorority | BA Dormitory
Public assembly Recreation | BA Exercise Center
Public order and safety Fire station/police station | BA Fire Station
Public assembly Recreation | BA Gymnasium
Outpatient health care PBA | BA Healthcare Clinic
Inpatient health care PBA | BA Hospital
Lodging Hotel | BA Hotel
Public assembly Library | BA Library
Nonrefrigerated warehouse Distribution/shipping center | BA Manufacturing Facility
Lodging Hotel | BA Motel
Public assembly Entertainment/culture | BA Motion Picture Theater
Lodging Other lodging | BA Multifamily
Public assembly Entertainment/culture | BA Museum
Office PBA | BA Office
Service (except Food) Vehicle storage/maintenance | BA Parking Garage
Public order and safety Other public order and safety | BA Penitentiary
Public assembly Entertainment/culture | BA Performing Arts Theater
Public order and safety Fire station/police station | BA Police Station
Service (except Food) Post office/postal center | BA Post Office
Religious worship PBA | BA Religious Building
Retail (except Malls) PBA | BA Retail
Education PBA | BA School/University
Public assembly PBA | BA Sports Arena
Public assembly PBA | BA Town Hall
Service (except Food) Other service | BA Transportation
Nonrefrigerated warehouse Non-refrigerated warehouse | BA Warehouse
Service (except Food) Repair shop | BA Workshop
Mapping to NREL41956 | Mapping to 90.1-2010
Other PBA | CS Atrium First 40 ft in Height
Other PBA | CS Atrium Height Above 40 ft
Public assembly PBA | CS Audience Seating Permanent Auditorium
Public assembly PBA | CS Audience Seating Permanent Motion Picture Theater
Public assembly PBA | CS Audience Seating Permanent Performing Arts Theater
Service (except Food) Vehicle service/repair shop | SS Automotive Service/Repair
Office Bank/other financial | SS Bank/Office Banking Activity Area
Education Other classroom education | CS Classroom/Lecture/Training
Public assembly Social/meeting | CS Conference/Meeting/Multipurpose
Public assembly PBA | SS Convention Center Audience Seating
Public assembly PBA | SS Convention Center Exhibit Space
Other PBA | CS Corridor/Transition
Public order and safety Other public order and safety | SS Courthouse/Police Station/Penitentiary Confinement Cells
Public order and safety Other public order and safety | SS Courthouse/Police Station/Penitentiary Courtroom
Public order and safety Other public order and safety | SS Courthouse/Police Station/Penitentiary Judges’ Chambers
Food service Restaurant/cafeteria | CS Dining Area General
Food service Restaurant/cafeteria | CS Dining Area Bar Lounge/Leisure Dining
Food service Other food service | CS Dining Area Family Dining
Lodging Dormitory/fraternity/sorority | SS Dormitory Living Quarters
Retail (except Malls) Other retail | CS Dressing/Fitting Room Performing Arts Theater
Vacant PBA | CS Electrical/Mechanical
Vacant PBA | CS Electrical/Mechanical
Public order and safety Fire station/police station | SS Fire Stations Engine Room
Public order and safety Fire station/police station | SS Fire Stations Sleeping Quarters
Food service Other food service | CS Food Preparation
Public assembly Recreation | SS Gymnasium/Fitness Center Fitness Area
Public assembly Recreation | SS Gymnasium/Fitness Center Gymnasium Audience Seating
Public assembly Recreation | SS Gymnasium/Fitness Center Playing Area
Nursing Nursing home/assisted living | SS Hotel/Highway Lodging Hotel Guest Rooms
Inpatient health care Hospital/inpatient health | SS Hospital Corridor/Transition
Inpatient health care Hospital/inpatient health | SS Hospital Emergency
Inpatient health care Hospital/inpatient health | SS Hospital Exam/Treatment
Inpatient health care Hospital/inpatient health | SS Hospital Laundry/Washing
Inpatient health care Hospital/inpatient health | SS Hospital Lounge/Recreation
Inpatient health care Hospital/inpatient health | SS Hospital Medical Supply
Inpatient health care Hospital/inpatient health | SS Hospital Nursery
Inpatient health care Hospital/inpatient health | SS Hospital Nurses’ Station
Inpatient health care Hospital/inpatient health | SS Hospital Operating Room
Inpatient health care Hospital/inpatient health | SS Hospital Patient Room
Inpatient health care Hospital/inpatient health | SS Hospital Pharmacy
Inpatient health care Hospital/inpatient health | SS Hospital Physical Therapy
Inpatient health care Hospital/inpatient health | SS Hospital Radiology/Imaging
Inpatient health care Hospital/inpatient health | SS Hospital Recovery
Food service Restaurant/cafeteria | SS Hotel/Highway Lodging Hotel Dining
Lodging Hotel | SS Hotel/Highway Lodging Hotel Guest Rooms
Public assembly Other public assembly | SS Hotel/Highway Lodging Hotel Lobby
Food service Restaurant/cafeteria | SS Hotel/Highway Lodging Highway Lodging Dining
Lodging Motel or inn | SS Hotel/Highway Lodging Highway Lodging Guest Rooms
Laboratory PBA | CS Laboratory Classrooms
Laboratory PBA | CS Laboratory Medical/Industrial/Research
Service (except Food) Other service | SS Hospital Laundry/Washing
Public assembly Library | SS Library Card File and Cataloging
Public assembly Library | SS Library Reading Area
Public assembly Library | SS Library Stacks
Public assembly Other public assembly | CS Lobby General
Public assembly Other public assembly | CS Lobby Elevator
Public assembly Entertainment/culture | CS Lobby Motion Picture Theater
Public assembly Entertainment/culture | CS Lobby Performing Arts Theater
Other PBA | CS Locker Room
Public assembly Recreation | CS Lounge/Recreation
Office PBA | CS Electrical/Mechanical
Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Corridor/Transition
Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Detailed Manufacturing
Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Equipment Room
Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Extra High Bay (>50 ft Floor to Ceiling Height)
Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing High Bay (25–50 ft Floor to Ceiling Height)
Nonrefrigerated warehouse Distribution/shipping center | SS Manufacturing Low Bay (<25 ft Floor to Ceiling Height)
Public assembly Entertainment/culture | SS Museum General Exhibition
Service (except Food) Repair shop | SS Museum Restoration
Nonrefrigerated warehouse PBA | CS Storage
Nonrefrigerated warehouse PBA | CS Storage
Office PBA | CS Office Enclosed
Office PBA | CS Office Open Plan
Service (except Food) Vehicle storage/maintenance | SS Parking Garage Garage Area
Public assembly Other public assembly | SS Courthouse/Police Station/Penitentiary Penitentiary Audience Seating
Education Other classroom education | SS Courthouse/Police Station/Penitentiary Penitentiary Classroom
Food service Restaurant/cafeteria | SS Courthouse/Police Station/Penitentiary Penitentiary Dining
Service (except Food) Post office/postal center | SS Post Office Sorting Area
Religious worship PBA | SS Religious Buildings Audience Seating
Religious worship PBA | SS Religious Buildings Fellowship Hall
Religious worship PBA | SS Religious Buildings Worship Pulpit, Choir
Other PBA | CS Restrooms
Other PBA | SS Retail Dressing/Fitting Room
Retail (except Malls) Other retail | SS Retail Mall Concourse
Retail (except Malls) Retail store | SS Retail Sales Area
Public assembly Other public assembly | SS Sports Arena Audience Seating
Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 1
Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 2
Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 3
Public assembly Recreation | SS Sports Arena Court Sports Arena—Class 4
Public assembly Recreation | SS Sports Arena Indoor Sports Fields
Public assembly Recreation | SS Sports Arena Ring Sports Arena
Other PBA | CS Stairway
Nonrefrigerated warehouse PBA | CS Storage
Nonrefrigerated warehouse PBA | CS Storage
Public assembly Other public assembly | SS Transportation Air/Train/Bus—Baggage Area
Public assembly Other public assembly | SS Transportation Airport—Concourse
Public assembly Other public assembly | SS Transportation Audience Seating
Public assembly Other public assembly | SS Transportation Terminal—Ticket Counter
Nonrefrigerated warehouse PBA | SS Warehouse Fine Material Storage
Nonrefrigerated warehouse PBA | SS Warehouse Medium/Bulky Material Storage
Refrigerated warehouse PBA | SS Warehouse Medium/Bulky Material Storage
Service (except Food) Repair shop | CS Workshop, General
Not assiogned
CS Sales Area

## OtherLists
Schedules Referenced on Modeling Data Tab and Contained in Appendix C
| Title | Letter | Examples
| C-1 Assembly | H | Convention center, exercise center, motion picture theature, performing arts theater, religious building, sports arena
| C-2 Public | E | Fire station, clinic, hospital, police station, transportation
| C-3 Hotel Motel | D | Hotel, motel, penitentiary
| C-4 Manufacturing | J | Automotive facility, workshop, manufacturing facility
| C-5 Office | A | courthouse, office, post office, town hall
| C-6 Parking Garage | K | Parking garage
| C-7 Restaurant | B | Cafeteria, fast food, family dining, bar, lounge
| C-8 Retail | C | Library, museum, retail
| C-9 Schools | G | K-12 schools, universities
| C-10 Warehouse | L | Warehouse
| C-11 Laboratory | X1 | Laboratory
| C-12 Residential | F | Dormatory, multifamily
| C-13 Data Center | X2 | Data center
| C-14 Gymnasium | I | Gymnasium
| Use parent schedule | ps | Schedule is inherited
Old Schedules No Longer Referenced
C-12 CEC Nonresidential
C-13 CEC Hotel Function
C-14 CEC Residential (setback)
C-15 CEC Residential (no setback)
C-16 CEC Retail
Building Types for Fenestration Limit
Grocery Store
Healthcare (outpatient)
Hospital
Hotel/motel (≤75 rooms)
Hotel/motel (>75 rooms)
Office (≤5000 ft2)
Office (5000 to 50,000 ft2)
Office (>50,000 ft2)
Restaurant (quick service)
Restaurant (full service)
Retail (stand alone)
Retail (strip mall)
School (primary)
School (secondary and university)
Warehouse (nonrefrigerated)
Building Types Used in HVAC Mapping
Residential
| Residential | Dormitories, hotels, motels, and multifamily buildings of four or more stories.
| Public Assembly | Houses of worship, auditoriums, movie theaters, performance theaters, concert halls, arenas, enclosed stadiums, ice rinks, gymnasiums, convention centers, exhibition centers, and natatoriums.
Retail
Hospitals
| Other Nonresidential | Buildings that are not public assembly, hospitals or low rise retail
Special Space Types used in HVAC Mapping
| Residential | Guest rooms, living quarters, private living space, and sleeping quarters (G3.1.1).
| Heated Only | Spaces with heating only systems in the proposed design, serving storage rooms, stairwells, vestibules, electrical/mechanical rooms, and restrooms not exhausting or transferring air from mechanically cooled thermal zones.
| Laboratories | Total laboratory exhaust rate greater than 15,000 cfm.
| Computer Rooms | > 3,000,000 Btu/h or >600,000 Btu/h where the baseline building system is 7 or 8