## 1
1 | Building Summary Large Hotel pre-1980 construction
UWG |  |  | PRE80 | PST80 | NEW
areaFloor |  | Total Floor Area (m2) | 11344.93 | 11344.93 | 11344.93
nFloor |  | Number of Floors | 6 | 6 | 6 | * Basement not counted
glazing |  | Total | 0.2663 | 0.2663 | 0.2663
hCeiling |  | Floor to Floor Height (m) | 3.2 | 3.2 | 3.2 | Average of 6 floors (not including basement)
areaWall |  | Gross Dimensions - Total Area (m2) | 4462.84 | 4462.84 | 4462.84
ver2hor |  | Wall to Skin Ratio | 0.75127 | 0.75127 | 0.75127
areaRoof |  | Gross Dimensions - Total Area (m2) | 1477.55 | 1477.55 | 1477.55
areaWindow |  | Total Area (m2) | 1214.07 | 1214.07 | 1214.07

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD3PRE | Total | Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 | 16.5137 | 17.08 | 18.3782 | 15229.9891 | 7.3772 | 1.2571 |  |  | 0.5031
BLD3PST | Total | Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 | 16.5137 | 17.08 | 18.3782 | 15229.9891 | 7.3772 | 1.2571 |  |  | 0.5031
BLD3PST | Total | Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 | 10.765 | 17.08 | 18.3782 | 15229.9891 | 7.3772 | 1.2571 |  |  | 0.13416

## 3
3 |  | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD3PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD3PRE | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD3PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD3PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD3PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD3PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD3PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD3PRE | HVAC |  | Air Conditioning (kW) | 1494.1123 | 1512.0242 | 1260.774 | 1354.1928 | 909.7562 | 987.0593 | 637.6085 | 1379.697 | 718.5799 | 706.2575 | 1272.3104 | 606.6903 | 1259.2054 | 571.6005 | 971.5788 | 509.5743
BLD3PRE | HEAT |  | HEATSYS1 BOILER | 2853.3571 | 3547.8467 | 3087.6181 | 3800.5772 | 2890.3308 | 3287.227 | 3102.263 | 4155.4364 | 3407.0826 | 3635.3411 | 4724.0541 | 3931.2693 | 5068.4706 | 4659.6448 | 5144.6648 | 6251.9205
BLD3PRE | COP |  | COOLSYS1 CHILLER 1 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
BLD3PRE | EffHeat |  | HEATSYS1 BOILER | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
BLD3PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 92.79 | 93.52 | 95.85 | 95.16 | 91.56 | 96.47 | 90.78 | 93.85 | 98.44 | 93.01 | 90.81 | 94.8 | 91.11 | 93.34 | 89.73 | 89.24
BLD3PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD3PST | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD3PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD3PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD3PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD3PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD3PST | HVAC |  | Air Conditioning (kW) | 1475.169 | 1405.2138 | 1215.63 | 1262.2039 | 901.0017 | 919.9698 | 610.742 | 1280.6757 | 613.6173 | 689.9516 | 1270.9274 | 608.9093 | 1204.0568 | 573.6523 | 988.3426 | 532.4302
BLD3PST | HEAT |  | HEATSYS1 BOILER | 2157.8931 | 2877.1676 | 2435.8301 | 3140.6752 | 2234.3423 | 2645.3089 | 2456.6815 | 3466.0462 | 2814.8411 | 2982.6092 | 4078.8929 | 3365.5417 | 4417.2371 | 4068.1662 | 4527.3688 | 5629.8293
BLD3PST | COP |  | COOLSYS1 CHILLER 1 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
BLD3PST | EffHeat |  | HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD3PST | Fan |  | Fan Max Flow Rate (m3/s ) | 89.47 | 89.54 | 91.83 | 91.31 | 89.45 | 91.63 | 87.14 | 90.19 | 95.74 | 90.68 | 91.16 | 95.67 | 91.54 | 94.3 | 92.46 | 94.81
BLD3NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD3NEW | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
BLD3NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD3NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD3NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD3NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD3NEW | HVAC |  | Air Conditioning (kW) | 1443.4134 | 1375.1917 | 1118.8005 | 1227.1329 | 834.7476 | 835.5216 | 601.7776 | 1250.6296 | 590.1525 | 652.2529 | 1238.7374 | 585.0039 | 1171.7152 | 545.4728 | 958.3593 | 481.0618
BLD3NEW | HEAT |  | HEATSYS1 BOILER | 2106.8007 | 2811.5062 | 2370.3824 | 3043.9012 | 2173.9682 | 2564.9428 | 2404.3016 | 3377.1861 | 2748.7006 | 2894.2612 | 3969.4165 | 3290.5072 | 4301.6083 | 3965.8732 | 4427.476 | 5422.9985
BLD3NEW | COP |  | COOLSYS1 CHILLER 1 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
BLD3NEW | EffHeat |  | HEATSYS1 BOILER | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD3NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 85.22 | 85.35 | 86.9 | 86.43 | 83.95 | 86.91 | 86.1 | 85.42 | 90.16 | 84.61 | 85.94 | 89.91 | 86.23 | 88.41 | 87.99 | 84.25

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
| Sun |  |  |  | SummerDesign | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 24
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
| Sat |  |  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
| Sun |  |  |  | SummerDesign | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 24
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
| Sat |  |  |  | SummerDesign | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 24
| Sun |  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
SetCool | All | Guest_CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
| All |  |  |  | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| All |  |  |  | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SetHeat | All | Guest_HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
| All |  |  |  | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| All |  |  |  | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
SchGas | WD | Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
| Sat |  |  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
| Sun |  |  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchSWH | WD | GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
| Sat |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
| Sun |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8

## BuildingSummary
1 | Building Summary Large Hotel pre-1980 construction
UWG |  |  | PRE80 | PST80 | NEW
Program
|  | Building Name | Large Hotel pre-1980 construction | Large Hotel post-1980 construction | Large Hotel new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Lodging | Lodging | Lodging
Form
areaFloor |  | Total Floor Area (m2) | 11344.93 | 11344.93 | 11344.93
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 3.8 1st floor, 5.1 other floors | 3.8 1st floor, 5.1 other floors | 3.8 1st floor, 5.1 other floors
nFloor |  | Number of Floors | 6 plus basement | 6 plus basement | 6 plus basement
Window Fraction (Window to Wall Ratio)
|  | South | 0.3254 | 0.3254 | 0.3254
|  | East | 0.2112 | 0.2112 | 0.2112
|  | North | 0.2311 | 0.2311 | 0.2311
|  | West | 0.2112 | 0.2112 | 0.2112
glazing |  | Total | 0.2663 | 0.2663 | 0.2663
|  | Skylight/TDD Percentage | 0 | 0 | 0
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | See pictures | See pictures | See pictures
|  | Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors | 3.96 1st floor, 3.05 other floors | 3.96 1st floor, 3.05 other floors
hCeiling |  | Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors | 3.96 1st floor, 3.05 other floors | 3.96 1st floor, 3.05 other floors
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Mass Wall | Mass Wall | Mass Wall
areaWall |  | Gross Dimensions - Total Area (m2) | 4462.84 | 4462.84 | 4462.84
|  | Net Dimensions - Total Area (m2) | 3248.53 | 3248.53 | 3248.53
ver2hor |  | Wall to Skin Ratio | 0.75127 | 0.75127 | 0.75127
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 1477.55 | 1477.55 | 1477.55
|  | Net Dimensions - Total Area (m2) | 1477.55 | 1477.55 | 1477.55
|  | Roof to Skin Ratio | 0.24873 | 0.24873 | 0.24873
Window Dimensions (m2)
|  | South | 609.46 | 609.46 | 609.46
|  | East | 85.84 | 85.84 | 85.84
|  | North | 432.93 | 432.93 | 432.93
|  | West | 85.84 | 85.84 | 85.84
areaWindow |  | Total Area (m2) | 1214.07 | 1214.07 | 1214.07
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Basement | Basement | Basement
|  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
|  | Dimensions - Total Area (m2) | 1978.83 | 1978.83 | 1978.83
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 15687.82 | 15687.82 | 15687.82
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 22690.58 | 22690.58 | 22690.58
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.59998 | 0.59998 | 0.15999
HVAC
|  | System Type | FCU in rooms, CV ventilation, MZCAV in common areas | FCU in rooms, CV ventilation, MZVAV in common areas | FCU in rooms, CV ventilation, MZVAV in common areas
|  | Heating Type | Gas boiler | Gas boiler | Gas boiler
|  | Cooling Type | 2 air cooled chillers | 2 air cooled chillers | 2 air cooled chillers
|  | Fan Control | Constant | Variable | Variable
Service Water Heating
|  | SWH Type | gas boiler | gas boiler | gas boiler
|  | Fuel | gas | gas | gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 44332.9 | 44332.9 | 44332.9

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 7.5347 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
|  | Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 38.099 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 1.0572
|  | Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 38.099 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.35236
|  | Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 8.6039 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.39384
|  | Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 3.9573 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.39382
|  | Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 12.2365 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 1.1318
|  | Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 15.7419 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.82991
|  | Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 20.2858 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.34234
|  | Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
|  | Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
|  | Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60879
|  | Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60863
|  | Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
|  | Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
|  | Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 13.1176 |  |  |  |  | 0.25 | 97.35 |  | 0.16612
|  | Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
|  | Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
|  | Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 3.4487
|  | Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
|  | Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
|  | Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 16.8341 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 1.132
|  | Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 13.081 |  |  |  |  | 0.25 | 103.03 |  | 0.44675
BLD3PRE | Total | Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 | 16.5137 | 17.08 | 18.3782 | 15229.9891 | 7.3772 | 1.2571 | 14262.067 |  | 0.5031
|  | Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 7.5347 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
|  | Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 38.099 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 1.0572
|  | Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 38.099 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.35236
|  | Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 8.6039 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.39384
|  | Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 3.9573 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.39382
|  | Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 12.2365 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 1.1318
|  | Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 15.7419 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.82991
|  | Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 20.2858 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.34234
|  | Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
|  | Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
|  | Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60879
|  | Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60863
|  | Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
|  | Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
|  | Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 13.1176 |  |  |  |  | 0.25 | 97.35 |  | 0.16612
|  | Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
|  | Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
|  | Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 3.4487
|  | Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
|  | Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
|  | Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 16.8341 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 1.132
|  | Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 13.081 |  |  |  |  | 0.25 | 103.03 |  | 0.44675
BLD3PST | Total | Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 | 16.5137 | 17.08 | 18.3782 | 15229.9891 | 7.3772 |  |  |  | 0.5031
|  | Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 10.7639 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
|  | Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 16.1458 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 0.28192
|  | Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 16.1458 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.093963
|  | Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 16.1458 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.10502
|  | Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 9.6875 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.10502
|  | Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 6.4583 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 0.30182
|  | Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 13.9931 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.22131
|  | Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 11.8403 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.091291
|  | Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.36556
|  | Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.3656
|  | Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 11.8403 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.16235
|  | Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 11.8403 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.1623
|  | Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.36556
|  | Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.3656
|  | Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 5.3819 |  |  |  |  | 0.25 | 97.35 |  | 0.044299
|  | Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.36556
|  | Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.8403 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 0.3656
|  | Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 11.8403 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 0.91966
|  | Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 13.9931 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.10503
|  | Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 13.9931 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.10503
|  | Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 12.9167 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 0.30186
|  | Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 5.3819 |  |  |  |  | 0.25 | 103.03 |  | 0.11913
BLD3PST | Total | Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 | 10.765 | 17.08 | 18.3782 | 15229.9891 | 7.3772 |  |  |  | 0.13416

## LocationSummary
3 |  | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD3PRE |  | Program
BLD3PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD3PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD3PRE
BLD3PRE |  | Fabric
BLD3PRE |  |  | Exterior walls - commercial space
BLD3PRE | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD3PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD3PRE |  |  | Exterior walls - residential space
BLD3PRE |  |  | Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
BLD3PRE |  |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD3PRE |  |  | Underground walls
BLD3PRE |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD3PRE |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675
BLD3PRE |  |  | Roof
BLD3PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD3PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD3PRE |  |  | Windows - fixed, commercial
BLD3PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD3PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD3PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD3PRE |  |  | Windows - operable, residential
BLD3PRE |  |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD3PRE |  |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD3PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD3PRE |  |  | Skylights/TDD
BLD3PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3PRE |  |  | Foundation
BLD3PRE |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD3PRE |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD3PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD3PRE |  | HVAC
BLD3PRE |  |  | HVAC Sizing
BLD3PRE | HVAC |  | Air Conditioning (kW) | 1494.1123 | 1512.0242 | 1260.774 | 1354.1928 | 909.7562 | 987.0593 | 637.6085 | 1379.697 | 718.5799 | 706.2575 | 1272.3104 | 606.6903 | 1259.2054 | 571.6005 | 971.5788 | 509.5743
BLD3PRE |  |  | COOLSYS1 CHILLER 1 | 747.0562 | 756.0121 | 630.387 | 677.0964 | 454.8781 | 493.5297 | 318.8042 | 689.8485 | 359.2899 | 353.1287 | 636.1552 | 303.3452 | 629.6027 | 285.8003 | 485.7894 | 254.7872
BLD3PRE |  |  | COOLSYS1 CHILLER 2 | 747.0562 | 756.0121 | 630.387 | 677.0964 | 454.8781 | 493.5297 | 318.8042 | 689.8485 | 359.2899 | 353.1287 | 636.1552 | 303.3452 | 629.6027 | 285.8003 | 485.7894 | 254.7872
BLD3PRE |  |  | Heating (kW)
BLD3PRE | HEAT |  | HEATSYS1 BOILER | 2853.3571 | 3547.8467 | 3087.6181 | 3800.5772 | 2890.3308 | 3287.227 | 3102.263 | 4155.4364 | 3407.0826 | 3635.3411 | 4724.0541 | 3931.2693 | 5068.4706 | 4659.6448 | 5144.6648 | 6251.9205
BLD3PRE |  |  | CORRIDOR_FLR_6 UNIT HEATER COIL | 5.774 | 13.2924 | 9.5946 | 16.5627 | 6.9952 | 12.5342 | 9.3845 | 17.6413 | 15.8021 | 13.2739 | 20.0543 | 18.389 | 21.2294 | 21.0153 | 22.6241 | 29.1742
BLD3PRE |  |  | HVAC Efficiency
BLD3PRE |  |  | Air Conditioning (COP)
BLD3PRE | COP |  | COOLSYS1 CHILLER 1 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
BLD3PRE |  |  | COOLSYS1 CHILLER 2 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
BLD3PRE |  |  | Heating Efficiency (%)
BLD3PRE | EffHeat |  | HEATSYS1 BOILER | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
BLD3PRE |  |  | CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD3PRE |  |  | HVAC Control - Economizer
BLD3PRE |  |  | FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
BLD3PRE |  |  | FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
BLD3PRE |  |  | CAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD3PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 92.79 | 93.52 | 95.85 | 95.16 | 91.56 | 96.47 | 90.78 | 93.85 | 98.44 | 93.01 | 90.81 | 94.8 | 91.11 | 93.34 | 89.73 | 89.24
BLD3PRE |  |  | CORRIDOR_FLR_6 UNIT HEATERFAN | 0.16 | 0.37 | 0.28 | 0.48 | 0.2 | 0.38 | 0.26 | 0.49 | 0.54 | 0.37 | 0.54 | 0.61 | 0.56 | 0.64 | 0.61 | 0.76
BLD3PRE |  |  | DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
BLD3PRE |  |  | KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
BLD3PRE |  |  | LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
BLD3PRE |  |  | ROOM_1_FLR_3 FAN COILFAN | 1.76 | 1.81 | 2.01 | 1.87 | 1.69 | 2.02 | 1.73 | 1.81 | 1.98 | 1.81 | 1.44 | 1.54 | 1.43 | 1.5 | 1.38 | 1.33
BLD3PRE |  |  | ROOM_1_FLR_6 FAN COILFAN | 0.51 | 0.53 | 0.58 | 0.54 | 0.48 | 0.58 | 0.48 | 0.51 | 0.56 | 0.5 | 0.4 | 0.43 | 0.39 | 0.4 | 0.37 | 0.35
BLD3PRE |  |  | ROOM_2_FLR_3 FAN COILFAN | 1.8 | 1.84 | 2.01 | 1.87 | 1.61 | 2.01 | 1.49 | 1.78 | 1.98 | 1.63 | 1.41 | 1.51 | 1.4 | 1.45 | 1.34 | 1.24
BLD3PRE |  |  | ROOM_2_FLR_6 FAN COILFAN | 0.52 | 0.53 | 0.58 | 0.54 | 0.46 | 0.58 | 0.41 | 0.51 | 0.56 | 0.46 | 0.39 | 0.42 | 0.38 | 0.39 | 0.36 | 0.33
BLD3PRE |  |  | ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
BLD3PRE |  |  | ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.63 | 1.82 | 2.2 | 2.01 | 2.05 | 2.23 | 2.63 | 2.07 | 2.03 | 2.65 | 1.48 | 1.52 | 1.5 | 1.59 | 1.48 | 2.06
BLD3PRE |  |  | ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
BLD3PRE |  |  | ROOM_5_FLR_3 FAN COILFAN | 1.5 | 1.52 | 1.71 | 1.59 | 1.43 | 1.66 | 1.43 | 1.55 | 1.61 | 1.56 | 1.21 | 1.24 | 1.23 | 1.24 | 1.16 | 1.2
BLD3PRE |  |  | ROOM_6_FLR_3 FAN COILFAN | 1.57 | 1.57 | 1.74 | 1.63 | 1.38 | 1.67 | 1.23 | 1.55 | 1.63 | 1.4 | 1.24 | 1.26 | 1.25 | 1.25 | 1.18 | 1.15
BLD3PRE |  |  | FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
BLD3PRE |  |  | FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
BLD3PRE |  |  | CAV WITH REHEAT_FAN | 37.78 | 37.97 | 39.18 | 39.07 | 36.7 | 39.78 | 35.56 | 38.02 | 41.99 | 37.07 | 37.14 | 40.71 | 37.41 | 39.32 | 36.29 | 35.26
BLD3PRE |  | Utility Costs
BLD3PRE |  |  | Electric Utility Rates
BLD3PRE |  |  | Average Annual Rate ($/kWh) | 0.072957 | 0.098768 | 0.066677 | 0.099375 | 0.041323 | 0.086017 | 0.12275 | 0.058392 | 0.036977 | 0.066648 | 0.095804 | 0.036982 | 0.053985 | 0.069603 | 0.054701 | 0.090831
BLD3PRE |  |  | Total Cost ($/m2) | 45.6 | 54.04 | 35.26 | 45.05 | 16.92 | 37.66 | 40.28 | 23.77 | 12.87 | 19.9 | 35.52 | 11.59 | 19.4 | 20.24 | 16.28 | 22.23
BLD3PRE |  |  | Gas Utility Rates
BLD3PRE |  |  | Average Annual Rate ($/MJ) | 0.011451 | 0.008183 | 0.0085607 | 0.010763 | 0.0084001 | 0.0081045 | 0.0084042 | 0.010076 | 0.0071925 | 0.0082864 | 0.0089279 | 0.0071994 | 0.0079839 | 0.00878 | 0.0079866 | 0.0042094
BLD3PRE |  |  | Total Cost ($/m2) | 5.08 | 4.52 | 4.22 | 7.09 | 5.1 | 4.59 | 5.9 | 7.67 | 5.26 | 6.54 | 7.6 | 5.97 | 7.46 | 8.17 | 8.42 | 5.25
BLD3PRE |  |  | Total Utility Costs
BLD3PRE |  |  | Cost Intensity ($/m2) | 50.68 | 58.56 | 39.48 | 52.14 | 22.03 | 42.25 | 46.18 | 31.44 | 18.13 | 26.44 | 43.12 | 17.56 | 26.85 | 28.41 | 24.71 | 27.48
BLD3PRE |  | Energy - End Uses
BLD3PRE |  |  | Electricity (kWh)
BLD3PRE |  |  | Heating | 0 | 33.3333 | 0 | 141.6667 | 0 | 0 | 0 | 325 | 0 | 0 | 394.4444 | 291.6667 | 1025 | 805.5556 | 2125 | 11733.3333
BLD3PRE |  |  | Cooling | 5082066.6667 | 4219777.7778 | 3990483.3333 | 3168288.8889 | 2680194.4444 | 2969744.4444 | 1774252.7778 | 2661205.5556 | 1962191.6667 | 1444936.1111 | 2268905.5556 | 1601777.7778 | 2140177.7778 | 1357763.8889 | 1452661.1111 | 851166.6667
BLD3PRE |  |  | Interior Lighting | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111
BLD3PRE |  |  | Exterior Lighting | 121627.7778 | 121580.5556 | 121558.3333 | 121538.8889 | 121447.2222 | 121419.4444 | 121483.3333 | 121408.3333 | 121455.5556 | 121213.8889 | 121427.7778 | 121358.3333 | 121350 | 121322.2222 | 121252.7778 | 120511.1111
BLD3PRE |  |  | Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
BLD3PRE |  |  | Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
BLD3PRE |  |  | Fans | 400194.4444 | 384802.7778 | 407511.1111 | 376900 | 371347.2222 | 400216.6667 | 356988.8889 | 362719.4444 | 391030.5556 | 353202.7778 | 345066.6667 | 362661.1111 | 343627.7778 | 351027.7778 | 333402.7778 | 326297.2222
BLD3PRE |  |  | Pumps | 30922.2222 | 25647.2222 | 24247.2222 | 21116.6667 | 19044.4444 | 20675 | 16094.4444 | 18719.4444 | 18788.8889 | 14997.2222 | 16755.5556 | 15705.5556 | 16433.3333 | 14936.1111 | 14213.8889 | 13425
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Refrigeration | 22238.8889 | 21477.7778 | 21633.3333 | 20783.3333 | 20841.6667 | 21105.5556 | 20200 | 20319.4444 | 20311.1111 | 19888.8889 | 20061.1111 | 19969.4444 | 19925 | 19675 | 19430.5556 | 19083.3333
BLD3PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 7090913.8889 | 6207183.3333 | 5999294.4444 | 5142633.3333 | 4646738.8889 | 4967025 | 3722883.3333 | 4618561.1111 | 3947644.4444 | 3388105.5556 | 4206475 | 3555625 | 4076402.7778 | 3299391.6667 | 3376950 | 2776080.5556
BLD3PRE |  |  | Gas (MJ)
BLD3PRE |  |  | Heating | 13930 | 242480 | 147880 | 492990 | 91660 | 280910 | 336750 | 893770 | 700830 | 819410 | 1254650 | 1033620 | 1614970 | 1476120 | 2038150 | 3088700
BLD3PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
BLD3PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 3783380 | 4783230 | 4208950 | 5746480 | 5559200 | 4901180 | 6383440 | 6503500 | 6359970 | 6897320 | 7168010 | 7133310 | 7742170 | 7846400 | 8689170 | 9835570
BLD3PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 5035950 | 6264360 | 5595480 | 7478110 | 6889510 | 6420740 | 7958830 | 8635930 | 8299450 | 8955380 | 9661310 | 9405580 | 10595790 | 10561170 | 11965970 | 14162920
BLD3PRE |  |  | Purchased Cooling (MJ)
BLD3PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Purchased Heating (MJ)
BLD3PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total Building (MJ) | 30563240 | 28610230 | 27192940 | 25991600 | 23617770 | 24302030 | 21361210 | 25262740 | 22510970 | 21152560 | 24804620 | 22205830 | 25270840 | 22438980 | 24122990 | 24156810
BLD3PRE |  | Energy - End Use Intensities
BLD3PRE |  |  | Electricity (MJ/m2)
BLD3PRE |  |  | Heating (elec) | 0 | 0.010577 | 0 | 0.044953 | 0 | 0 | 0 | 0.10313 | 0 | 0 | 0.12516 | 0.092549 | 0.32525 | 0.25561 | 0.67429 | 3.7231
BLD3PRE |  |  | Cooling (elec) | 1612.6022 | 1338.9874 | 1266.2294 | 1005.337 | 850.4586 | 942.3364 | 562.9922 | 844.4332 | 622.6275 | 458.496 | 719.9516 | 508.2638 | 679.1047 | 430.8352 | 460.9472 | 270.0856
BLD3PRE |  |  | Interior Lighting (elec) | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946
BLD3PRE |  |  | Exterior Lighting (elec) | 38.594 | 38.579 | 38.572 | 38.5658 | 38.5367 | 38.5279 | 38.5482 | 38.5244 | 38.5393 | 38.4627 | 38.5305 | 38.5085 | 38.5058 | 38.497 | 38.475 | 38.2397
BLD3PRE |  |  | Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
BLD3PRE |  |  | Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
BLD3PRE |  |  | Fans (elec) | 126.9866 | 122.1027 | 129.3083 | 119.595 | 117.833 | 126.9937 | 113.277 | 115.0953 | 124.0788 | 112.0756 | 109.4939 | 115.0768 | 109.0373 | 111.3854 | 105.7928 | 103.5381
BLD3PRE |  |  | Pumps (elec) | 9.812 | 8.1382 | 7.6939 | 6.7006 | 6.043 | 6.5604 | 5.107 | 5.9399 | 5.9619 | 4.7588 | 5.3167 | 4.9836 | 5.2145 | 4.7394 | 4.5102 | 4.2599
BLD3PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Refrigeration (elec) | 7.0567 | 6.8152 | 6.8645 | 6.5948 | 6.6133 | 6.6971 | 6.4097 | 6.4476 | 6.445 | 6.311 | 6.3656 | 6.3366 | 6.3224 | 6.2431 | 6.1656 | 6.0554
BLD3PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 2250.0342 | 1969.6156 | 1903.6499 | 1631.8208 | 1474.4674 | 1576.0981 | 1181.3167 | 1465.5262 | 1252.6361 | 1075.0875 | 1334.7662 | 1128.2435 | 1293.4927 | 1046.9375 | 1071.5478 | 880.8845
BLD3PRE |  |  | Gas (MJ/m2)
BLD3PRE |  |  | Heating (gas) | 1.2278 | 21.3727 | 13.0345 | 43.4533 | 8.0791 | 24.7601 | 29.6819 | 78.7789 | 61.7728 | 72.2247 | 110.5877 | 91.1056 | 142.3472 | 130.1086 | 179.6472 | 272.2451
BLD3PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
BLD3PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems (gas) | 333.4758 | 421.6049 | 370.9866 | 506.508 | 490.0007 | 432.0013 | 562.6511 | 573.2335 | 560.5824 | 607.9457 | 631.8049 | 628.7464 | 682.4127 | 691.5998 | 765.8835 | 866.9298
BLD3PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 443.8802 | 552.1551 | 493.1985 | 659.1378 | 607.2573 | 565.9388 | 701.5096 | 761.1908 | 731.5326 | 789.3478 | 851.5701 | 829.0295 | 933.9373 | 930.8859 | 1054.7082 | 1248.3524
BLD3PRE |  |  | Purchased Cooling (MJ/m2)
BLD3PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Purchased Heating (MJ/m2)
BLD3PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Total Building (MJ/m2) | 2693.9144 | 2521.7716 | 2396.8484 | 2290.9595 | 2081.7247 | 2142.0369 | 1882.8263 | 2226.7161 | 1984.1688 | 1864.4354 | 2186.3364 | 1957.273 | 2227.4301 | 1977.8234 | 2126.2559 | 2129.2369
BLD3PRE |  | Peak Energy Demand
BLD3PRE |  |  | Electricity Peak Demand (kW)
BLD3PRE |  |  | Jan | 1081.0159 | 1078.701 | 968.2755 | 903.7733 | 796.7976 | 721.8043 | 654.5865 | 611.3113 | 654.9418 | 551.6269 | 589.5279 | 650.0136 | 542.8826 | 558.5837 | 516.6652 | 505.1188
BLD3PRE |  |  | Feb | 1079.1158 | 1095.1526 | 973.5511 | 894.7235 | 789.5063 | 823.2144 | 664.5473 | 586.9195 | 700.6747 | 676.0002 | 579.0037 | 648.9655 | 569.4513 | 634.1698 | 564.3966 | 505.9616
BLD3PRE |  |  | Mar | 1093.0055 | 1096.3244 | 1002.7869 | 1028.7392 | 790.1299 | 836.1976 | 664.7324 | 1047.6866 | 703.3144 | 694.6332 | 875.7449 | 653.6521 | 740.6117 | 634.4132 | 581.6771 | 587.1854
BLD3PRE |  |  | Apr | 1103.0646 | 1096.279 | 1003.4541 | 1026.3405 | 802.6543 | 854.3526 | 663.9924 | 1035.1076 | 705.1925 | 695.8785 | 860.279 | 651.0676 | 957.658 | 634.6861 | 693.4105 | 585.6287
BLD3PRE |  |  | May | 1103.1738 | 1106.8453 | 1014.6826 | 1031.9902 | 789.8052 | 853.4162 | 664.4834 | 1046.1479 | 706.8869 | 696.3803 | 995.8669 | 651.4526 | 983.6592 | 636.5038 | 818.2905 | 581.0134
BLD3PRE |  |  | Jun | 1089.8219 | 1079.4249 | 1022.7388 | 1039.6884 | 792.7933 | 857.6858 | 664.22 | 1035.983 | 707.492 | 695.084 | 999.7557 | 650.7333 | 976.7651 | 606.5976 | 823.6058 | 578.5247
BLD3PRE |  |  | Jul | 1066.4917 | 1099.1563 | 1022.8122 | 1021.1503 | 787.1671 | 857.6204 | 664.1467 | 1034.65 | 708.669 | 696.4492 | 985.2503 | 648.8136 | 973.4767 | 625.972 | 817.6203 | 576.4966
BLD3PRE |  |  | Aug | 1066.0056 | 1088.9004 | 1023.4842 | 1012.8366 | 783.3364 | 859.273 | 666.4033 | 1054.8097 | 709.9097 | 696.5121 | 975.231 | 652.407 | 972.0155 | 633.6936 | 827.6101 | 579.6175
BLD3PRE |  |  | Sep | 1066.7557 | 1114.8715 | 1017.3462 | 1006.3018 | 791.0619 | 851.7508 | 662.9468 | 1037.4292 | 705.6783 | 697.3455 | 990.6998 | 651.1118 | 968.5783 | 634.5388 | 819.4933 | 606.0414
BLD3PRE |  |  | Oct | 1085.4107 | 1074.0337 | 1001.954 | 1015.2625 | 796.4047 | 847.6525 | 664.0913 | 1029.7643 | 705.037 | 697.2354 | 980.1178 | 650.9001 | 949.0381 | 637.6887 | 799.6917 | 606.3176
BLD3PRE |  |  | Nov | 1091.2621 | 1078.99 | 975.6724 | 975.0652 | 793.0295 | 830.039 | 667.3264 | 1014.3479 | 703.5585 | 669.716 | 986.6597 | 649.7353 | 771.7616 | 636.2853 | 622.4247 | 513.4287
BLD3PRE |  |  | Dec | 1085.7498 | 1081.6201 | 966.5768 | 853.7146 | 803.2201 | 800.4275 | 649.8846 | 559.346 | 623.3998 | 535.4109 | 592.1439 | 612.3011 | 542.85 | 569.715 | 521.5521 | 451.7571
BLD3PRE |  |  | Time of Peak Electrical Demand
BLD3PRE |  |  | Jan | 04-JAN-20:30 | 02-JAN-20:00 | 27-JAN-20:10 | 24-JAN-21:00 | 26-JAN-20:10 | 29-JAN-08:00 | 27-JAN-20:19 | 08-JAN-20:00 | 26-JAN-20:19 | 27-JAN-21:00 | 17-JAN-21:00 | 24-JAN-20:10 | 30-JAN-21:00 | 30-JAN-21:00 | 16-JAN-20:00 | 21-JAN-20:00
BLD3PRE |  |  | Feb | 17-FEB-20:10 | 22-FEB-20:00 | 27-FEB-20:10 | 18-FEB-18:10 | 23-FEB-20:10 | 27-FEB-20:10 | 13-FEB-20:10 | 15-FEB-20:19 | 13-FEB-20:10 | 21-FEB-20:10 | 20-FEB-20:00 | 10-FEB-20:40 | 19-FEB-20:00 | 03-FEB-20:10 | 22-FEB-21:00 | 28-FEB-20:10
BLD3PRE |  |  | Mar | 14-MAR-19:10 | 21-MAR-19:10 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:10 | 22-MAR-19:10 | 29-MAR-19:10 | 09-MAR-20:19 | 31-MAR-19:10 | 28-MAR-19:10 | 31-MAR-18:10 | 31-MAR-19:00 | 19-MAR-19:00 | 09-MAR-20:49 | 22-MAR-19:40 | 29-MAR-19:30
BLD3PRE |  |  | Apr | 19-APR-19:10 | 04-APR-19:10 | 26-APR-19:10 | 13-APR-19:10 | 11-APR-19:10 | 28-APR-19:10 | 27-APR-19:10 | 05-APR-19:10 | 19-APR-19:10 | 14-APR-19:10 | 28-APR-17:19 | 10-APR-19:19 | 16-APR-19:10 | 13-APR-19:10 | 04-APR-19:10 | 28-APR-20:00
BLD3PRE |  |  | May | 05-MAY-19:10 | 11-MAY-19:10 | 19-MAY-19:19 | 26-MAY-19:40 | 09-MAY-19:10 | 31-MAY-19:10 | 02-MAY-19:10 | 05-MAY-19:10 | 15-MAY-19:10 | 01-MAY-19:19 | 04-MAY-19:10 | 30-MAY-19:19 | 15-MAY-19:30 | 10-MAY-19:00 | 31-MAY-19:49 | 12-MAY-19:00
BLD3PRE |  |  | Jun | 02-JUN-19:10 | 23-JUN-19:30 | 27-JUN-19:00 | 12-JUN-19:49 | 29-JUN-19:00 | 21-JUN-19:10 | 08-JUN-19:00 | 21-JUN-19:40 | 13-JUN-19:19 | 08-JUN-19:00 | 15-JUN-19:30 | 01-JUN-19:19 | 22-JUN-19:00 | 15-JUN-19:10 | 15-JUN-19:00 | 07-JUN-19:10
BLD3PRE |  |  | Jul | 24-JUL-19:00 | 28-JUL-19:19 | 10-JUL-19:00 | 11-JUL-19:49 | 28-JUL-19:10 | 06-JUL-19:10 | 06-JUL-19:49 | 20-JUL-19:30 | 12-JUL-19:19 | 12-JUL-19:00 | 21-JUL-19:19 | 10-JUL-19:30 | 03-JUL-19:00 | 31-JUL-19:00 | 26-JUL-19:49 | 05-JUL-19:10
BLD3PRE |  |  | Aug | 24-AUG-19:10 | 11-AUG-19:10 | 01-AUG-19:00 | 29-AUG-19:10 | 23-AUG-19:10 | 09-AUG-19:10 | 02-AUG-19:19 | 18-AUG-19:10 | 24-AUG-19:40 | 31-AUG-19:10 | 01-AUG-19:10 | 23-AUG-19:10 | 29-AUG-19:10 | 02-AUG-19:00 | 23-AUG-19:10 | 31-AUG-19:10
BLD3PRE |  |  | Sep | 08-SEP-19:00 | 26-SEP-19:10 | 11-SEP-19:10 | 12-SEP-19:10 | 20-SEP-19:10 | 11-SEP-19:10 | 18-SEP-19:10 | 08-SEP-19:10 | 08-SEP-19:10 | 06-SEP-19:10 | 26-SEP-19:10 | 15-SEP-19:19 | 13-SEP-19:10 | 21-SEP-19:10 | 06-SEP-19:10 | 20-SEP-19:10
BLD3PRE |  |  | Oct | 24-OCT-19:10 | 19-OCT-19:10 | 02-OCT-19:10 | 06-OCT-19:10 | 20-OCT-19:00 | 06-OCT-19:10 | 06-OCT-19:10 | 20-OCT-19:10 | 25-OCT-19:10 | 05-OCT-19:10 | 11-OCT-19:19 | 02-OCT-19:10 | 08-OCT-19:10 | 20-OCT-19:00 | 07-OCT-19:10 | 03-OCT-19:00
BLD3PRE |  |  | Nov | 16-NOV-20:10 | 24-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 07-NOV-20:10 | 21-NOV-20:10 | 02-NOV-19:10 | 03-NOV-19:10 | 09-NOV-20:10 | 04-NOV-19:10 | 02-NOV-19:10 | 10-NOV-20:10 | 02-NOV-15:09 | 21-NOV-20:10 | 02-NOV-20:00 | 14-NOV-21:00
BLD3PRE |  |  | Dec | 28-DEC-20:10 | 20-DEC-20:30 | 13-DEC-20:00 | 04-DEC-20:00 | 29-DEC-20:10 | 05-DEC-19:19 | 17-DEC-20:10 | 03-DEC-20:00 | 05-DEC-20:19 | 25-DEC-20:00 | 11-DEC-21:00 | 22-DEC-20:00 | 01-DEC-21:00 | 31-DEC-20:00 | 01-DEC-20:00 | 19-DEC-21:00
BLD3PRE |  | Source Energy
BLD3PRE |  |  | Total Source Energy (GJ) | 90173.28 | 88000.86 | 74423.03 | 70445.46 | 59297.3 | 70972.81 | 50171.41 | 68887.93 | 56216.81 | 31026.77 | 64248.32 | 52742.13 | 62008.76 | 52820.05 | 54850.52 | 51164.08
BLD3PRE |  |  | Total Source Energy (MJ/m2) | 7948.08 | 7756.6 | 6559.82 | 6209.23 | 5226.6 | 6255.71 | 4422.22 | 6071.94 | 4955.08 | 2734.77 | 5663 | 4648.81 | 5465.6 | 4655.68 | 4834.65 | 4509.72
BLD3PRE |  | Water Consumption (m3)
BLD3PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
BLD3PRE |  |  | Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
BLD3PRE |  | Emissions
BLD3PRE |  |  | Carbon Equivalent (kg) | 2035490 | 2183440 | 1911940 | 1718970 | 667281.3899 | 1791040 | 578597.0804 | 1402070 | 1762270 | 408259.4792 | 2416900 | 1622070 | 1586400 | 1396170 | 1371690 | 1036550
BLD3PRE |  |  | CO2 (kg) | 4765390 | 5521790 | 4550540 | 3984930 | 1808780 | 4302380 | 1576240 | 3244900 | 4189930 | 1052770 | 5677820 | 3874420 | 3768810 | 3354590 | 3288250 | 2694690
BLD3PRE |  |  | NOX (kg) | 8179.7402 | 7125.2002 | 7463.0998 | 7296.2708 | 1566.6087 | 6810.7008 | 1370.5072 | 5996.7523 | 6985.2862 | 1365.4558 | 9879.1474 | 6382.9208 | 6371.2017 | 5477.5319 | 5428.7983 | 3121.4069
BLD3PRE |  |  | SO2 (kg) | 30353.296 | 29609.948 | 24125.863 | 18052.6498 | 13523.2956 | 27324.3246 | 10835.2757 | 16861.9064 | 17240.793 | 2621.1347 | 28350.8657 | 15529.2268 | 9623.8039 | 8812.5992 | 7973.3488 | 14135.1546
BLD3PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PRE |  |  | Hg (kg) | 0.1388 | 0.0839 | 0.066 | 0.0667 | 0.0068 | 0.0519 | 0.0057 | 0.0688 | 0.068 | 0.0112 | 0.0865 | 0.0615 | 0.0713 | 0.0622 | 0.0594 | 0.0493
BLD3PRE |  |  | Water for Electricity (m3) | 3756.47 | 10099.8 | 178205 | 32108.5 | 81586.3 | 136265 | 65365.5 | 1048.59 | 17925.5 | 34615.6 | 6526.09 | 16145.4 | 6324.3 | 208997 | 5239.14 | 2836.27
BLD3PST |  | Location Summary
BLD3PST |  |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD3PST |  | Program
BLD3PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD3PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD3PST
BLD3PST |  | Fabric
BLD3PST |  |  | Exterior walls - commercial space
BLD3PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD3PST | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD3PST |  |  | Exterior walls - residential space
BLD3PST |  |  | Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
BLD3PST |  |  | R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD3PST |  |  | Underground walls
BLD3PST |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD3PST |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 1.5385 | 0.30675 | 0.30675 | 1.5385 | 1.8904 | 1.7123 | 1.8904 | 2.0661 | 2.0661 | 2.4155 | 2.2422 | 2.5974 | 3.125
BLD3PST |  |  | Roof
BLD3PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD3PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD3PST |  |  | Windows - fixed, commercial
BLD3PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD3PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD3PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD3PST |  |  | Windows - operable, residential
BLD3PST |  |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD3PST |  |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD3PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD3PST |  |  | Skylights/TDD
BLD3PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3PST |  |  | Foundation
BLD3PST |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD3PST |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD3PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD3PST |  | HVAC
BLD3PST |  |  | HVAC Sizing
BLD3PST | HVAC |  | Air Conditioning (kW) | 1475.169 | 1405.2138 | 1215.63 | 1262.2039 | 901.0017 | 919.9698 | 610.742 | 1280.6757 | 613.6173 | 689.9516 | 1270.9274 | 608.9093 | 1204.0568 | 573.6523 | 988.3426 | 532.4302
BLD3PST |  |  | COOLSYS1 CHILLER 1 | 737.5845 | 702.6069 | 607.815 | 631.102 | 450.5009 | 459.9849 | 305.371 | 640.3378 | 306.8086 | 344.9758 | 635.4637 | 304.4547 | 602.0284 | 286.8262 | 494.1713 | 266.2151
BLD3PST |  |  | COOLSYS1 CHILLER 2 | 737.5845 | 702.6069 | 607.815 | 631.102 | 450.5009 | 459.9849 | 305.371 | 640.3378 | 306.8086 | 344.9758 | 635.4637 | 304.4547 | 602.0284 | 286.8262 | 494.1713 | 266.2151
BLD3PST |  |  | Heating (kW)
BLD3PST | HEAT |  | HEATSYS1 BOILER | 2157.8931 | 2877.1676 | 2435.8301 | 3140.6752 | 2234.3423 | 2645.3089 | 2456.6815 | 3466.0462 | 2814.8411 | 2982.6092 | 4078.8929 | 3365.5417 | 4417.2371 | 4068.1662 | 4527.3688 | 5629.8293
BLD3PST |  |  | CORRIDOR_FLR_6 UNIT HEATER COIL | 5.5576 | 11.8899 | 7.7688 | 14.1897 | 7.6304 | 9.8006 | 9.2563 | 13.1945 | 12.6222 | 10.4816 | 16.9624 | 15.3253 | 17.4642 | 17.9083 | 17.7842 | 21.4869
BLD3PST |  |  | HVAC Efficiency
BLD3PST |  |  | Air Conditioning (COP)
BLD3PST | COP |  | COOLSYS1 CHILLER 1 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
BLD3PST |  |  | COOLSYS1 CHILLER 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
BLD3PST |  |  | Heating Efficiency (%)
BLD3PST | EffHeat |  | HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD3PST |  |  | CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD3PST |  |  | HVAC Control - Economizer
BLD3PST |  |  | FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
BLD3PST |  |  | FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
BLD3PST |  |  | VAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD3PST | Fan |  | Fan Max Flow Rate (m3/s ) | 89.47 | 89.54 | 91.83 | 91.31 | 89.45 | 91.63 | 87.14 | 90.19 | 95.74 | 90.68 | 91.16 | 95.67 | 91.54 | 94.3 | 92.46 | 94.81
BLD3PST |  |  | CORRIDOR_FLR_6 UNIT HEATERFAN | 0.15 | 0.33 | 0.22 | 0.4 | 0.22 | 0.28 | 0.26 | 0.33 | 0.41 | 0.27 | 0.43 | 0.48 | 0.43 | 0.51 | 0.44 | 0.49
BLD3PST |  |  | DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
BLD3PST |  |  | KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
BLD3PST |  |  | LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
BLD3PST |  |  | ROOM_1_FLR_3 FAN COILFAN | 1.34 | 1.36 | 1.58 | 1.3 | 1.55 | 1.51 | 1.37 | 1.3 | 1.53 | 1.39 | 1.36 | 1.48 | 1.35 | 1.42 | 1.5 | 1.68
BLD3PST |  |  | ROOM_1_FLR_6 FAN COILFAN | 0.37 | 0.37 | 0.41 | 0.36 | 0.43 | 0.39 | 0.37 | 0.35 | 0.41 | 0.38 | 0.36 | 0.39 | 0.35 | 0.37 | 0.39 | 0.44
BLD3PST |  |  | ROOM_2_FLR_3 FAN COILFAN | 1.36 | 1.37 | 1.57 | 1.29 | 1.46 | 1.49 | 1.19 | 1.29 | 1.52 | 1.31 | 1.35 | 1.46 | 1.33 | 1.4 | 1.46 | 1.56
BLD3PST |  |  | ROOM_2_FLR_6 FAN COILFAN | 0.37 | 0.37 | 0.41 | 0.36 | 0.41 | 0.39 | 0.32 | 0.35 | 0.41 | 0.36 | 0.36 | 0.39 | 0.35 | 0.37 | 0.38 | 0.41
BLD3PST |  |  | ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
BLD3PST |  |  | ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.36 | 1.39 | 1.57 | 1.43 | 1.82 | 1.52 | 2.03 | 1.3 | 1.39 | 1.93 | 1.31 | 1.33 | 1.34 | 1.44 | 1.59 | 2.65
BLD3PST |  |  | ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
BLD3PST |  |  | ROOM_5_FLR_3 FAN COILFAN | 1.12 | 1.13 | 1.31 | 1.12 | 1.25 | 1.22 | 1.07 | 1.12 | 1.24 | 1.21 | 1.17 | 1.2 | 1.18 | 1.21 | 1.29 | 1.55
BLD3PST |  |  | ROOM_6_FLR_3 FAN COILFAN | 1.17 | 1.17 | 1.34 | 1.15 | 1.22 | 1.24 | 0.95 | 1.15 | 1.28 | 1.15 | 1.19 | 1.23 | 1.2 | 1.23 | 1.3 | 1.47
BLD3PST |  |  | FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
BLD3PST |  |  | FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
BLD3PST |  |  | VAV WITH REHEAT_FAN | 36.67 | 36.49 | 37.86 | 38.34 | 35.53 | 38.03 | 34.02 | 37.44 | 41.99 | 37.12 | 38.07 | 42.15 | 38.45 | 40.79 | 38.55 | 39
BLD3PST |  | Utility Costs
BLD3PST |  |  | Electric Utility Rates
BLD3PST |  |  | Average Annual Rate ($/kWh) | 0.072333 | 0.098509 | 0.066648 | 0.099304 | 0.041362 | 0.086312 | 0.12326 | 0.056194 | 0.036979 | 0.06615 | 0.096232 | 0.036981 | 0.052968 | 0.069078 | 0.053534 | 0.089836
BLD3PST |  |  | Total Cost ($/m2) | 47.67 | 53.92 | 35.13 | 45.34 | 17.08 | 36.09 | 39.62 | 24.13 | 12.24 | 20.87 | 37.77 | 11.79 | 20.19 | 21.09 | 17.68 | 24.4
BLD3PST |  |  | Gas Utility Rates
BLD3PST |  |  | Average Annual Rate ($/MJ) | 0.011451 | 0.0081735 | 0.0085404 | 0.010616 | 0.0084064 | 0.0080689 | 0.00842 | 0.010014 | 0.0071612 | 0.0083047 | 0.0088124 | 0.0071606 | 0.0079621 | 0.0086554 | 0.0079592 | 0.0041817
BLD3PST |  |  | Total Cost ($/m2) | 5.35 | 5.08 | 4.61 | 8.25 | 5.43 | 5.13 | 6.54 | 9.34 | 6.01 | 7.8 | 9.59 | 7.06 | 9.81 | 10.06 | 11.23 | 7.71
BLD3PST |  |  | Total Utility Costs
BLD3PST |  |  | Cost Intensity ($/m2) | 53.01 | 59 | 39.75 | 53.59 | 22.51 | 41.22 | 46.16 | 33.47 | 18.25 | 28.67 | 47.36 | 18.85 | 30 | 31.16 | 28.92 | 32.11
BLD3PST |  | Energy - End Uses
BLD3PST |  |  | Electricity (kWh)
BLD3PST |  |  | Heating | 400 | 341.6667 | 1311.1111 | 119.4444 | 27.7778 | 858.3333 | 0 | 58.3333 | 152.7778 | 0 | 86.1111 | 72.2222 | 175 | 205.5556 | 175 | 1169.4444
BLD3PST |  |  | Cooling | 5548369.4444 | 4289858.3333 | 4053141.6667 | 3266430.5556 | 2772277.7778 | 2825097.2222 | 1745588.8889 | 2962100 | 1834988.8889 | 1672211.1111 | 2544022.2222 | 1702650 | 2414741.6667 | 1552463.8889 | 1836216.6667 | 1157341.6667
BLD3PST |  |  | Interior Lighting | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111
BLD3PST |  |  | Exterior Lighting | 121627.7778 | 121580.5556 | 121558.3333 | 121538.8889 | 121447.2222 | 121419.4444 | 121483.3333 | 121408.3333 | 121455.5556 | 121213.8889 | 121427.7778 | 121358.3333 | 121350 | 121322.2222 | 121252.7778 | 120511.1111
BLD3PST |  |  | Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
BLD3PST |  |  | Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
BLD3PST |  |  | Fans | 318902.7778 | 316733.3333 | 325644.4444 | 316088.8889 | 317691.6667 | 322130.5556 | 310130.5556 | 313741.6667 | 324927.7778 | 316783.3333 | 315313.8889 | 322411.1111 | 315944.4444 | 320441.6667 | 319813.8889 | 330916.6667
BLD3PST |  |  | Pumps | 31280.5556 | 26244.4444 | 23616.6667 | 21677.7778 | 18827.7778 | 19872.2222 | 15619.4444 | 20041.6667 | 18483.3333 | 15697.2222 | 18516.6667 | 16691.6667 | 19061.1111 | 16572.2222 | 17341.6667 | 18672.2222
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Refrigeration | 21830.5556 | 21077.7778 | 21208.3333 | 20419.4444 | 20608.3333 | 20686.1111 | 20005.5556 | 19969.4444 | 19969.4444 | 19611.1111 | 19633.3333 | 19594.4444 | 19488.8889 | 19283.3333 | 19027.7778 | 18630.5556
BLD3PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 7476277.7778 | 6209700 | 5980344.4444 | 5180141.6667 | 4684747.2222 | 4743925 | 3646694.4444 | 4871186.1111 | 3753841.6667 | 3579380.5556 | 4452863.8889 | 3616641.6667 | 4324625 | 3464152.7778 | 3747691.6667 | 3081102.7778
BLD3PST |  |  | Gas (MJ)
BLD3PST |  |  | Heating | 180310 | 909270 | 573960 | 1687040 | 393770 | 950500 | 1030990 | 2676960 | 1767110 | 2349060 | 3752730 | 2634960 | 4798200 | 3904590 | 5862750 | 9597950
BLD3PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
BLD3PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 3880220 | 4905880 | 4316720 | 5893750 | 5701720 | 5026760 | 6547090 | 6670230 | 6523020 | 7074150 | 7351750 | 7316160 | 7940640 | 8047570 | 8911920 | 10087700
BLD3PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 5299180 | 7053810 | 6129320 | 8819430 | 7334130 | 7215910 | 8816730 | 10585840 | 9528780 | 10661860 | 12343130 | 11189770 | 13977490 | 13190810 | 16013330 | 20924300
BLD3PST |  |  | Purchased Cooling (MJ)
BLD3PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Purchased Heating (MJ)
BLD3PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total Building (MJ) | 32213770 | 29408720 | 27658560 | 27467940 | 24199220 | 24294040 | 21944830 | 28122110 | 23042610 | 23547620 | 28373440 | 24209680 | 29546140 | 25661760 | 29505020 | 32016270
BLD3PST |  | Energy - End Use Intensities
BLD3PST |  |  | Electricity (MJ/m2)
BLD3PST |  |  | Heating (elec) | 0.12692 | 0.10842 | 0.41603 | 0.037901 | 0.0088142 | 0.27236 | 0 | 0.01851 | 0.048478 | 0 | 0.027324 | 0.022917 | 0.05553 | 0.065225 | 0.05553 | 0.37108
BLD3PST |  |  | Cooling (elec) | 1760.5658 | 1361.2248 | 1286.1117 | 1036.4786 | 879.6778 | 896.4381 | 553.8968 | 939.9107 | 582.2645 | 530.6131 | 807.2495 | 540.2718 | 766.2272 | 492.6159 | 582.6541 | 367.2387
BLD3PST |  |  | Interior Lighting (elec) | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946
BLD3PST |  |  | Exterior Lighting (elec) | 38.594 | 38.579 | 38.572 | 38.5658 | 38.5367 | 38.5279 | 38.5482 | 38.5244 | 38.5393 | 38.4627 | 38.5305 | 38.5085 | 38.5058 | 38.497 | 38.475 | 38.2397
BLD3PST |  |  | Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
BLD3PST |  |  | Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
BLD3PST |  |  | Fans (elec) | 101.1918 | 100.5034 | 103.331 | 100.2989 | 100.8075 | 102.216 | 98.4082 | 99.5541 | 103.1036 | 100.5192 | 100.053 | 102.305 | 100.2531 | 101.6801 | 101.4809 | 105.0039
BLD3PST |  |  | Pumps (elec) | 9.9257 | 8.3277 | 7.4939 | 6.8786 | 5.9743 | 6.3057 | 4.9562 | 6.3595 | 5.865 | 4.9809 | 5.8756 | 5.2965 | 6.0483 | 5.2586 | 5.5027 | 5.9249
BLD3PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Refrigeration (elec) | 6.9271 | 6.6882 | 6.7297 | 6.4793 | 6.5393 | 6.564 | 6.348 | 6.3366 | 6.3366 | 6.2228 | 6.2299 | 6.2176 | 6.1841 | 6.1188 | 6.0377 | 5.9117
BLD3PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 2372.3149 | 1970.4142 | 1897.6368 | 1643.7226 | 1486.5279 | 1505.3057 | 1157.141 | 1545.6872 | 1191.1401 | 1135.7815 | 1412.9485 | 1147.6049 | 1372.2567 | 1099.2183 | 1189.1886 | 977.6718
BLD3PST |  |  | Gas (MJ/m2)
BLD3PST |  |  | Heating (gas) | 15.8929 | 80.1452 | 50.5902 | 148.6996 | 34.7078 | 83.7793 | 90.8738 | 235.9534 | 155.7571 | 207.0516 | 330.7743 | 232.2514 | 422.9244 | 344.1596 | 516.7563 | 845.9854
BLD3PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
BLD3PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems (gas) | 342.0115 | 432.4156 | 380.4856 | 519.4887 | 502.5627 | 443.0702 | 577.0756 | 587.9294 | 574.954 | 623.5319 | 648.0002 | 644.8632 | 699.9063 | 709.3314 | 785.5172 | 889.1531
BLD3PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 467.0819 | 621.7391 | 540.2524 | 777.3649 | 646.4471 | 636.0269 | 777.1269 | 933.0603 | 839.8886 | 939.7609 | 1087.9519 | 986.2921 | 1232.0082 | 1162.6684 | 1411.4518 | 1844.316
BLD3PST |  |  | Purchased Cooling (MJ/m2)
BLD3PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Purchased Heating (MJ/m2)
BLD3PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Total Building (MJ/m2) | 2839.3959 | 2592.1523 | 2437.8892 | 2421.0875 | 2132.975 | 2141.3327 | 1934.2679 | 2478.7476 | 2031.0287 | 2075.5415 | 2500.9004 | 2133.897 | 2604.2649 | 2261.8867 | 2600.6404 | 2821.9878
BLD3PST |  | Peak Energy Demand
BLD3PST |  |  | Electricity Peak Demand (kW)
BLD3PST |  |  | Jan | 1100.4761 | 1057.789 | 965.3219 | 969.8062 | 801.982 | 637.7233 | 658.0453 | 841.979 | 652.2122 | 595.5682 | 614.3543 | 659.3479 | 586.7091 | 598.6618 | 573.5975 | 571.517
BLD3PST |  |  | Feb | 1095.314 | 1066.1164 | 969.91 | 928.8236 | 801.1514 | 807.681 | 662.2872 | 757.4908 | 661.0856 | 700.211 | 603.9428 | 658.8534 | 606.2435 | 642.062 | 615.5919 | 576.599
BLD3PST |  |  | Mar | 1109.0482 | 1070.1959 | 995.9766 | 1001.6984 | 798.4397 | 817.163 | 662.2786 | 1013.9565 | 664.5038 | 697.0703 | 965.7849 | 663.2302 | 807.0064 | 642.9856 | 636.9027 | 633.087
BLD3PST |  |  | Apr | 1119.3192 | 1069.4441 | 998.9036 | 998.1161 | 804.7235 | 827.5502 | 660.7534 | 1005.5886 | 664.2845 | 698.1017 | 918.0862 | 660.7977 | 949.7109 | 646.4875 | 781.9034 | 636.0293
BLD3PST |  |  | May | 1121.745 | 1078.2581 | 1009.2206 | 1004.805 | 800.6928 | 827.6109 | 662.0386 | 1013.8309 | 659.7062 | 698.5882 | 1012.1848 | 660.2761 | 972.0955 | 644.2153 | 839.1184 | 596.7389
BLD3PST |  |  | Jun | 1106.9889 | 1047.5771 | 1013.1747 | 1011.5166 | 802.1693 | 830.6617 | 660.8381 | 1010.5048 | 657.8428 | 696.9861 | 1022.0161 | 659.791 | 967.8857 | 612.2114 | 843.1469 | 594.0578
BLD3PST |  |  | Jul | 1077.3315 | 1066.2891 | 1012.6168 | 995.1505 | 792.8552 | 829.0899 | 661.8324 | 1006.2129 | 653.1453 | 695.3974 | 1005.3357 | 650.223 | 963.8509 | 626.762 | 840.3981 | 590.8024
BLD3PST |  |  | Aug | 1080.0185 | 1056.9242 | 1013.7459 | 988.1757 | 791.0654 | 830.9943 | 662.0408 | 1029.9134 | 655.0145 | 695.6691 | 995.2419 | 654.1288 | 963.0554 | 639.5381 | 846.5654 | 596.2419
BLD3PST |  |  | Sep | 1078.7189 | 1084.0718 | 1008.6938 | 982.1084 | 798.3723 | 824.79 | 658.6121 | 1009.9006 | 658.5039 | 700.0881 | 1010.6319 | 660.7425 | 958.782 | 643.5672 | 840.6421 | 634.6215
BLD3PST |  |  | Oct | 1104.8019 | 1045.9319 | 994.2802 | 992.1522 | 804.9594 | 821.1303 | 659.6905 | 992.0426 | 666.1321 | 698.8061 | 1001.071 | 660.1065 | 959.8222 | 645.8619 | 819.2665 | 630.4927
BLD3PST |  |  | Nov | 1105.3662 | 1052.9852 | 969.9086 | 981.2645 | 803.5364 | 813.6091 | 664.417 | 980.765 | 661.7805 | 683.8685 | 1004.9164 | 660.0639 | 765.6553 | 645.4132 | 673.3382 | 573.8902
BLD3PST |  |  | Dec | 1104.3867 | 1061.7814 | 964.6402 | 957.2248 | 813.9423 | 784.7742 | 648.4282 | 777.0209 | 627.2495 | 588.8892 | 618.0566 | 623.6751 | 588.2346 | 605.0895 | 576.2186 | 534.3859
BLD3PST |  |  | Time of Peak Electrical Demand
BLD3PST |  |  | Jan | 04-JAN-20:10 | 18-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:10 | 12-JAN-20:10 | 18-JAN-20:00 | 17-JAN-20:49 | 09-JAN-06:10 | 26-JAN-20:30 | 27-JAN-21:00 | 17-JAN-21:00 | 24-JAN-20:19 | 30-JAN-21:00 | 30-JAN-21:00 | 15-JAN-20:00 | 20-JAN-21:00
BLD3PST |  |  | Feb | 17-FEB-20:10 | 22-FEB-20:00 | 27-FEB-20:10 | 22-FEB-07:10 | 23-FEB-20:10 | 27-FEB-20:10 | 13-FEB-20:00 | 14-FEB-06:30 | 13-FEB-20:10 | 21-FEB-20:10 | 27-FEB-21:00 | 10-FEB-20:00 | 19-FEB-20:00 | 03-FEB-20:10 | 22-FEB-21:00 | 28-FEB-20:10
BLD3PST |  |  | Mar | 14-MAR-19:10 | 21-MAR-19:10 | 17-MAR-19:10 | 28-MAR-19:10 | 28-MAR-19:10 | 22-MAR-19:10 | 30-MAR-19:10 | 09-MAR-20:10 | 31-MAR-19:30 | 28-MAR-19:10 | 31-MAR-18:10 | 31-MAR-19:00 | 23-MAR-17:19 | 15-MAR-19:10 | 22-MAR-19:19 | 28-MAR-19:00
BLD3PST |  |  | Apr | 19-APR-19:10 | 04-APR-19:10 | 26-APR-19:10 | 13-APR-19:10 | 11-APR-19:10 | 28-APR-19:10 | 20-APR-19:10 | 05-APR-19:10 | 28-APR-19:10 | 26-APR-19:10 | 28-APR-17:10 | 28-APR-19:19 | 27-APR-19:10 | 04-APR-19:49 | 04-APR-18:10 | 05-APR-19:49
BLD3PST |  |  | May | 05-MAY-19:10 | 11-MAY-19:10 | 19-MAY-19:19 | 26-MAY-19:40 | 08-MAY-19:10 | 31-MAY-19:10 | 15-MAY-19:10 | 05-MAY-19:10 | 05-MAY-19:10 | 01-MAY-19:19 | 04-MAY-19:10 | 12-MAY-19:49 | 15-MAY-19:30 | 10-MAY-19:00 | 31-MAY-19:49 | 12-MAY-19:00
BLD3PST |  |  | Jun | 02-JUN-19:10 | 23-JUN-19:30 | 20-JUN-19:40 | 12-JUN-19:49 | 08-JUN-19:10 | 21-JUN-19:10 | 12-JUN-19:00 | 05-JUN-19:30 | 12-JUN-19:00 | 08-JUN-19:00 | 15-JUN-19:30 | 01-JUN-19:00 | 22-JUN-19:00 | 12-JUN-19:10 | 15-JUN-19:00 | 07-JUN-19:10
BLD3PST |  |  | Jul | 24-JUL-19:00 | 28-JUL-19:19 | 06-JUL-19:40 | 11-JUL-19:49 | 28-JUL-19:10 | 06-JUL-19:10 | 06-JUL-19:30 | 20-JUL-19:30 | 06-JUL-19:19 | 12-JUL-19:00 | 21-JUL-19:19 | 27-JUL-19:30 | 03-JUL-19:00 | 31-JUL-19:00 | 28-JUL-19:49 | 05-JUL-19:10
BLD3PST |  |  | Aug | 04-AUG-19:10 | 11-AUG-19:10 | 23-AUG-19:10 | 29-AUG-19:10 | 01-AUG-19:00 | 09-AUG-19:10 | 03-AUG-19:19 | 18-AUG-19:10 | 24-AUG-19:19 | 30-AUG-19:00 | 01-AUG-19:10 | 04-AUG-19:00 | 29-AUG-19:10 | 22-AUG-19:40 | 23-AUG-19:10 | 31-AUG-19:10
BLD3PST |  |  | Sep | 08-SEP-19:00 | 26-SEP-19:10 | 07-SEP-19:10 | 13-SEP-19:10 | 20-SEP-19:10 | 11-SEP-19:10 | 18-SEP-19:00 | 08-SEP-19:10 | 08-SEP-19:10 | 19-SEP-19:10 | 26-SEP-19:10 | 15-SEP-19:40 | 15-SEP-19:10 | 20-SEP-19:10 | 06-SEP-19:10 | 28-SEP-19:00
BLD3PST |  |  | Oct | 24-OCT-19:10 | 26-OCT-19:10 | 02-OCT-19:10 | 12-OCT-19:10 | 20-OCT-19:30 | 06-OCT-19:10 | 06-OCT-19:10 | 20-OCT-19:10 | 04-OCT-19:10 | 05-OCT-19:10 | 11-OCT-19:10 | 02-OCT-19:10 | 02-OCT-19:10 | 20-OCT-19:00 | 07-OCT-19:10 | 04-OCT-19:00
BLD3PST |  |  | Nov | 16-NOV-20:10 | 24-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 24-NOV-20:10 | 21-NOV-20:10 | 06-NOV-20:10 | 03-NOV-19:10 | 13-NOV-20:40 | 03-NOV-19:00 | 02-NOV-19:10 | 03-NOV-19:10 | 02-NOV-15:09 | 21-NOV-20:10 | 02-NOV-20:00 | 14-NOV-21:00
BLD3PST |  |  | Dec | 28-DEC-20:10 | 20-DEC-20:49 | 13-DEC-20:00 | 04-DEC-20:00 | 29-DEC-20:10 | 05-DEC-19:19 | 17-DEC-20:10 | 08-DEC-06:30 | 05-DEC-20:30 | 31-DEC-20:00 | 11-DEC-21:00 | 22-DEC-21:00 | 01-DEC-21:00 | 31-DEC-20:00 | 01-DEC-21:00 | 18-DEC-07:00
BLD3PST |  | Source Energy
BLD3PST |  |  | Total Source Energy (GJ) | 95062.42 | 88895.81 | 74790.2 | 72364.4 | 60206.32 | 68968.24 | 50259.35 | 74269.43 | 55244.31 | 34089.75 | 70322.17 | 55419.29 | 68772.86 | 57753.38 | 63857.49 | 62469.85
BLD3PST |  |  | Total Source Energy (MJ/m2) | 8379.02 | 7835.48 | 6592.18 | 6378.37 | 5306.73 | 6079.02 | 4429.98 | 6546.28 | 4869.36 | 3004.75 | 6198.36 | 4884.79 | 6061.8 | 5090.52 | 5628.55 | 5506.24
BLD3PST |  | Water Consumption (m3)
BLD3PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
BLD3PST |  |  | Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
BLD3PST |  | Emissions
BLD3PST |  |  | Carbon Equivalent (kg) | 2145930 | 2198510 | 1915850 | 1754710 | 679741.0293 | 1730130 | 585163.6146 | 1505410 | 1705270 | 452963.1235 | 2596620 | 1679170 | 1732340 | 1503800 | 1571570 | 1244310
BLD3PST |  |  | CO2 (kg) | 5023820 | 5565020 | 4564900 | 4081030 | 1843810 | 4165590 | 1597160 | 3499370 | 4069510 | 1174770 | 6120630 | 4025450 | 4140870 | 3631630 | 3791670 | 3261960
BLD3PST |  |  | NOX (kg) | 8623.7824 | 7165.3073 | 7465.6124 | 7410.349 | 1597.7881 | 6556.0442 | 1390.7428 | 6394.6497 | 6719.7755 | 1499.3447 | 10557.8874 | 6569.2121 | 6888.5942 | 5850.4999 | 6154.1066 | 3710.5793
BLD3PST |  |  | SO2 (kg) | 32002.877 | 29622.1535 | 24049.8032 | 18184.6572 | 13634.0154 | 26097.3176 | 10613.8098 | 17784.6117 | 16394.8252 | 2769.4314 | 30012.0432 | 15796.1488 | 10210.5512 | 9253.2374 | 8849.4437 | 15689.6517
BLD3PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3PST |  |  | Hg (kg) | 0.1464 | 0.084 | 0.0659 | 0.0673 | 0.0069 | 0.0497 | 0.0057 | 0.0728 | 0.0649 | 0.0119 | 0.0918 | 0.0627 | 0.0759 | 0.0656 | 0.0662 | 0.0553
BLD3PST |  |  | Water for Electricity (m3) | 3960.62 | 10103.9 | 177643 | 32342.7 | 82253.6 | 130145 | 64027.8 | 1105.94 | 17045.4 | 36569.8 | 6908.35 | 16422.4 | 6709.4 | 219434 | 5814.32 | 3147.9
BLD3NEW |  | Location Summary
BLD3NEW |  |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD3NEW |  | Program
BLD3NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD3NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD3NEW |  |  | Weighting Factor | 11.7809 | 67.2676 | 13.5344 | 68.8195 |  | 85.905 | 11.4406 | 103.8454 | 4.0102 | 13.276 | 99.5961 | 21.6382 | 24.5558 | 6.2509 | 4.15 | 0.38782
BLD3NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD3NEW |  |  | Exterior walls - commercial space
BLD3NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD3NEW | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
BLD3NEW |  |  | Exterior walls - residential space
BLD3NEW |  |  | Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
BLD3NEW |  |  | R-value (m2·K / W) | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.692 | 1.9569 | 1.9569 | 1.9569 | 1.9569 | 2.2026 | 2.4814
BLD3NEW |  |  | Underground walls
BLD3NEW |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD3NEW |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 1.6313 | 1.6313
BLD3NEW |  |  | Roof
BLD3NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD3NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD3NEW |  |  | Windows - fixed, commercial
BLD3NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD3NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD3NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD3NEW |  |  | Windows - operable, residential
BLD3NEW |  |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD3NEW |  |  | SHGC | 0.251 | 0.251 | 0.251 | 0.385 | 0.385 | 0.385 | 0.61 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD3NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.305 | 0.305 | 0.305 | 0.474 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD3NEW |  |  | Skylights/TDD
BLD3NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD3NEW |  |  | Foundation
BLD3NEW |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD3NEW |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD3NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD3NEW |  | HVAC
BLD3NEW |  |  | HVAC Sizing
BLD3NEW | HVAC |  | Air Conditioning (kW) | 1443.4134 | 1375.1917 | 1118.8005 | 1227.1329 | 834.7476 | 835.5216 | 601.7776 | 1250.6296 | 590.1525 | 652.2529 | 1238.7374 | 585.0039 | 1171.7152 | 545.4728 | 958.3593 | 481.0618
BLD3NEW |  |  | COOLSYS1 CHILLER 1 | 721.7067 | 687.5958 | 559.4003 | 613.5664 | 417.3738 | 417.7608 | 300.8888 | 625.3148 | 295.0762 | 326.1265 | 619.3687 | 292.502 | 585.8576 | 272.7364 | 479.1796 | 240.5309
BLD3NEW |  |  | COOLSYS1 CHILLER 2 | 721.7067 | 687.5958 | 559.4003 | 613.5664 | 417.3738 | 417.7608 | 300.8888 | 625.3148 | 295.0762 | 326.1265 | 619.3687 | 292.502 | 585.8576 | 272.7364 | 479.1796 | 240.5309
BLD3NEW |  |  | Heating (kW)
BLD3NEW | HEAT |  | HEATSYS1 BOILER | 2106.8007 | 2811.5062 | 2370.3824 | 3043.9012 | 2173.9682 | 2564.9428 | 2404.3016 | 3377.1861 | 2748.7006 | 2894.2612 | 3969.4165 | 3290.5072 | 4301.6083 | 3965.8732 | 4427.476 | 5422.9985
BLD3NEW |  |  | CORRIDOR_FLR_6 UNIT HEATER COIL | 4.0479 | 9.8537 | 6.9689 | 10.7942 | 4.21 | 8.0817 | 6.6791 | 12.5042 | 10.9518 | 9.3651 | 16.6262 | 14.8857 | 19.0169 | 18.9434 | 20.2532 | 22.642
BLD3NEW |  |  | HVAC Efficiency
BLD3NEW |  |  | Air Conditioning (COP)
BLD3NEW | COP |  | COOLSYS1 CHILLER 1 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
BLD3NEW |  |  | COOLSYS1 CHILLER 2 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
BLD3NEW |  |  | Heating Efficiency (%)
BLD3NEW | EffHeat |  | HEATSYS1 BOILER | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD3NEW |  |  | CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD3NEW |  |  | HVAC Control - Economizer
BLD3NEW |  |  | FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
BLD3NEW |  |  | FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
BLD3NEW |  |  | VAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD3NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 85.22 | 85.35 | 86.9 | 86.43 | 83.95 | 86.91 | 86.1 | 85.42 | 90.16 | 84.61 | 85.94 | 89.91 | 86.23 | 88.41 | 87.99 | 84.25
BLD3NEW |  |  | CORRIDOR_FLR_6 UNIT HEATERFAN | 0.1 | 0.26 | 0.19 | 0.28 | 0.1 | 0.22 | 0.17 | 0.31 | 0.34 | 0.23 | 0.42 | 0.47 | 0.48 | 0.56 | 0.53 | 0.53
BLD3NEW |  |  | DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
BLD3NEW |  |  | KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
BLD3NEW |  |  | LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
BLD3NEW |  |  | ROOM_1_FLR_3 FAN COILFAN | 1.13 | 1.16 | 1.31 | 1.24 | 1.12 | 1.34 | 1.7 | 1.2 | 1.33 | 1.19 | 1.22 | 1.31 | 1.22 | 1.28 | 1.38 | 1
BLD3NEW |  |  | ROOM_1_FLR_6 FAN COILFAN | 0.31 | 0.33 | 0.37 | 0.35 | 0.32 | 0.38 | 0.47 | 0.34 | 0.38 | 0.33 | 0.34 | 0.37 | 0.34 | 0.36 | 0.38 | 0.26
BLD3NEW |  |  | ROOM_2_FLR_3 FAN COILFAN | 1.15 | 1.17 | 1.31 | 1.24 | 1.1 | 1.33 | 1.46 | 1.2 | 1.33 | 1.12 | 1.21 | 1.3 | 1.2 | 1.25 | 1.34 | 0.94
BLD3NEW |  |  | ROOM_2_FLR_6 FAN COILFAN | 0.32 | 0.33 | 0.37 | 0.35 | 0.31 | 0.38 | 0.41 | 0.34 | 0.38 | 0.31 | 0.34 | 0.37 | 0.33 | 0.35 | 0.37 | 0.25
BLD3NEW |  |  | ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
BLD3NEW |  |  | ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.15 | 1.16 | 1.39 | 1.2 | 1.15 | 1.3 | 2.52 | 1.17 | 1.23 | 1.59 | 1.19 | 1.22 | 1.24 | 1.32 | 1.51 | 1.45
BLD3NEW |  |  | ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
BLD3NEW |  |  | ROOM_5_FLR_3 FAN COILFAN | 0.98 | 0.98 | 1.12 | 1.07 | 0.94 | 1.12 | 1.4 | 1.03 | 1.09 | 0.99 | 1.04 | 1.07 | 1.05 | 1.06 | 1.16 | 0.88
BLD3NEW |  |  | ROOM_6_FLR_3 FAN COILFAN | 1.02 | 1.02 | 1.15 | 1.1 | 0.96 | 1.14 | 1.2 | 1.06 | 1.12 | 0.97 | 1.06 | 1.09 | 1.07 | 1.08 | 1.17 | 0.88
BLD3NEW |  |  | FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
BLD3NEW |  |  | FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
BLD3NEW |  |  | VAV WITH REHEAT_FAN | 33.5 | 33.38 | 34.13 | 34.04 | 32.39 | 34.14 | 31.21 | 33.21 | 37.4 | 32.32 | 33.56 | 37.15 | 33.74 | 35.59 | 34.59 | 32.5
BLD3NEW |  | Utility Costs
BLD3NEW |  |  | Electric Utility Rates
BLD3NEW |  |  | Average Annual Rate ($/kWh) | 0.073177 | 0.098654 | 0.069199 | 0.10514 | 0.11998 | 0.086047 | 0.14258 | 0.066366 | 0.037005 | 0.06578 | 0.097254 | 0.037008 | 0.052631 | 0.06901 | 0.052951 | 0.08908
BLD3NEW |  |  | Total Cost ($/m2) | 26.54 | 30.96 | 20.36 | 29.41 | 30.32 | 22.04 | 31.01 | 17.28 | 8.13 | 13.79 | 23.66 | 7.85 | 12.37 | 13.95 | 11.28 | 16.47
BLD3NEW |  |  | Gas Utility Rates
BLD3NEW |  |  | Average Annual Rate ($/MJ) | 0.011451 | 0.0081755 | 0.0085451 | 0.010667 | 0.0084033 | 0.008082 | 0.0084137 | 0.010027 | 0.007167 | 0.0082999 | 0.0088354 | 0.0071664 | 0.0079652 | 0.0086709 | 0.0079624 | 0.0041874
BLD3NEW |  |  | Total Cost ($/m2) | 5.23 | 4.89 | 4.47 | 7.8 | 5.33 | 4.92 | 6.28 | 8.8 | 5.8 | 7.37 | 8.98 | 6.78 | 9.17 | 9.61 | 10.54 | 6.98
BLD3NEW |  |  | Total Utility Costs
BLD3NEW |  |  | Cost Intensity ($/m2) | 31.77 | 35.85 | 24.83 | 37.21 | 35.65 | 26.96 | 37.29 | 26.08 | 13.93 | 21.15 | 32.64 | 14.63 | 21.54 | 23.57 | 21.82 | 23.45
BLD3NEW |  | Energy - End Uses
BLD3NEW |  |  | Electricity (kWh)
BLD3NEW |  |  | Heating | 13.8889 | 38.8889 | 838.8889 | 5.5556 | 0 | 483.3333 | 0 | 47.2222 | 2.7778 | 0 | 247.2222 | 183.3333 | 1072.2222 | 761.1111 | 1630.5556 | 3950
BLD3NEW |  |  | Cooling | 2473577.7778 | 1922511.1111 | 1696519.4444 | 1539083.3333 | 1240972.2222 | 1267744.4444 | 829913.8889 | 1325252.7778 | 855319.4444 | 754883.3333 | 1132000 | 775008.3333 | 1037511.1111 | 664219.4444 | 784025 | 473508.3333
BLD3NEW |  |  | Interior Lighting | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111
BLD3NEW |  |  | Exterior Lighting | 73227.7778 | 73200 | 73186.1111 | 73175 | 73119.4444 | 73102.7778 | 73141.6667 | 73097.2222 | 73125 | 72977.7778 | 73108.3333 | 73066.6667 | 73061.1111 | 73044.4444 | 73000 | 72555.5556
BLD3NEW |  |  | Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
BLD3NEW |  |  | Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
BLD3NEW |  |  | Fans | 309716.6667 | 307955.5556 | 315072.2222 | 310077.7778 | 304750 | 314225 | 319327.7778 | 306825 | 315902.7778 | 305997.2222 | 306986.1111 | 313541.6667 | 307527.7778 | 311105.5556 | 312308.3333 | 301847.2222
BLD3NEW |  |  | Pumps | 27263.8889 | 25947.2222 | 22369.4444 | 21572.2222 | 18236.1111 | 19922.2222 | 16083.3333 | 19786.1111 | 17569.4444 | 15366.6667 | 18391.6667 | 16661.1111 | 18725 | 16461.1111 | 17183.3333 | 17794.4444
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Refrigeration | 21802.7778 | 21111.1111 | 21261.1111 | 20502.7778 | 20577.7778 | 20786.1111 | 20044.4444 | 20041.6667 | 20063.8889 | 19686.1111 | 19719.4444 | 19705.5556 | 19552.7778 | 19372.2222 | 19105.5556 | 18755.5556
BLD3NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 4114788.8889 | 3559950 | 3338433.3333 | 3173602.7778 | 2866844.4444 | 2905452.7778 | 2467694.4444 | 2954238.8889 | 2491172.2222 | 2378100 | 2759638.8889 | 2407352.7778 | 2666638.8889 | 2294152.7778 | 2416441.6667 | 2097600
BLD3NEW |  |  | Gas (MJ)
BLD3NEW |  |  | Heating | 163130 | 764610 | 488420 | 1309170 | 398120 | 771390 | 847750 | 2210560 | 1582800 | 1932820 | 3123500 | 2363710 | 4075290 | 3490640 | 5096210 | 7836740
BLD3NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
BLD3NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 3783270 | 4783250 | 4208800 | 5746390 | 5559180 | 4901120 | 6383390 | 6503480 | 6359940 | 6897280 | 7167980 | 7133270 | 7742140 | 7846380 | 8689130 | 9835500
BLD3NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 5185050 | 6786510 | 5935860 | 8294210 | 7195950 | 6911160 | 8469800 | 9952690 | 9181400 | 10068750 | 11530130 | 10735640 | 13056070 | 12575670 | 15023990 | 18910900
BLD3NEW |  |  | Purchased Cooling (MJ)
BLD3NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Purchased Heating (MJ)
BLD3NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total Building (MJ) | 19998290 | 19602330 | 17954220 | 19719180 | 17516590 | 17370780 | 17353500 | 20587950 | 18149620 | 18629910 | 21464830 | 19402110 | 22655970 | 20834620 | 23723180 | 26462260
BLD3NEW |  | Energy - End Use Intensities
BLD3NEW |  |  | Electricity (MJ/m2)
BLD3NEW |  |  | Heating (elec) | 0.0044071 | 0.01234 | 0.26619 | 0.0017628 | 0 | 0.15337 | 0 | 0.014984 | 0.00088142 | 0 | 0.078447 | 0.058174 | 0.34023 | 0.24151 | 0.5174 | 1.2534
BLD3NEW |  |  | Cooling (elec) | 784.8966 | 610.0364 | 538.3265 | 488.3701 | 393.7757 | 402.2709 | 263.3419 | 420.519 | 271.4034 | 239.5338 | 359.1975 | 245.9197 | 329.215 | 210.765 | 248.7808 | 150.25
BLD3NEW |  |  | Interior Lighting (elec) | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025
BLD3NEW |  |  | Exterior Lighting (elec) | 23.2361 | 23.2273 | 23.2229 | 23.2193 | 23.2017 | 23.1964 | 23.2088 | 23.1946 | 23.2035 | 23.1567 | 23.1982 | 23.185 | 23.1832 | 23.1779 | 23.1638 | 23.0228
BLD3NEW |  |  | Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
BLD3NEW |  |  | Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
BLD3NEW |  |  | Fans (elec) | 98.2769 | 97.7181 | 99.9763 | 98.3915 | 96.7009 | 99.7075 | 101.3266 | 97.3593 | 100.2398 | 97.0967 | 97.4105 | 99.4906 | 97.5823 | 98.7176 | 99.0993 | 95.7798
BLD3NEW |  |  | Pumps (elec) | 8.6512 | 8.2334 | 7.0981 | 6.8451 | 5.7865 | 6.3216 | 5.1034 | 6.2784 | 5.575 | 4.876 | 5.8359 | 5.2868 | 5.9417 | 5.2233 | 5.4525 | 5.6464
BLD3NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Refrigeration (elec) | 6.9183 | 6.6988 | 6.7464 | 6.5058 | 6.5296 | 6.5957 | 6.3603 | 6.3595 | 6.3665 | 6.2466 | 6.2572 | 6.2528 | 6.2043 | 6.147 | 6.0624 | 5.9514
BLD3NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 1305.6731 | 1129.6159 | 1059.3259 | 1007.0232 | 909.685 | 921.9359 | 783.0298 | 937.4163 | 790.4796 | 754.6004 | 875.6673 | 763.8826 | 846.1573 | 727.9629 | 766.7666 | 665.5943
BLD3NEW |  |  | Gas (MJ/m2)
BLD3NEW |  |  | Heating (gas) | 14.3787 | 67.3945 | 43.0505 | 115.3933 | 35.0912 | 67.9921 | 74.7226 | 194.8439 | 139.5116 | 170.3632 | 275.3125 | 208.3428 | 359.2055 | 307.6731 | 449.1917 | 690.7483
BLD3NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
BLD3NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems (gas) | 333.4661 | 421.6067 | 370.9733 | 506.5001 | 489.9989 | 431.996 | 562.6467 | 573.2317 | 560.5798 | 607.9422 | 631.8023 | 628.7429 | 682.4101 | 691.598 | 765.8799 | 866.9236
BLD3NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 457.0223 | 598.1786 | 523.2004 | 731.0708 | 634.2676 | 609.1656 | 746.5477 | 877.253 | 809.2697 | 887.4828 | 1016.2922 | 946.264 | 1150.7921 | 1108.4485 | 1324.2491 | 1666.8503
BLD3NEW |  |  | Purchased Cooling (MJ/m2)
BLD3NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Purchased Heating (MJ/m2)
BLD3NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Total Building (MJ/m2) | 1762.6954 | 1727.7945 | 1582.5263 | 1738.094 | 1543.9526 | 1531.1006 | 1529.5775 | 1814.6693 | 1599.7493 | 1642.0832 | 1891.9596 | 1710.1467 | 1996.9494 | 1836.4114 | 2091.0157 | 2332.4446
BLD3NEW |  | Peak Energy Demand
BLD3NEW |  |  | Electricity Peak Demand (kW)
BLD3NEW |  |  | Jan | 629.8168 | 612.833 | 556.7552 | 570.8259 | 488.6012 | 438.5513 | 433.8267 | 485.0101 | 432.1967 | 396.7003 | 404.3948 | 425.9744 | 387.0716 | 395.0553 | 383.7391 | 381.1546
BLD3NEW |  |  | Feb | 632.6148 | 618.0988 | 559.1268 | 552.5027 | 486.8169 | 486.9656 | 437.7043 | 435.8438 | 432.9252 | 442.7436 | 401.0728 | 425.9757 | 394.9423 | 421.2039 | 402.5641 | 382.8915
BLD3NEW |  |  | Mar | 638.6441 | 611.3742 | 572.2468 | 587.4108 | 486.9552 | 489.7227 | 437.6897 | 594.0613 | 434.292 | 446.2392 | 548.3611 | 431.9056 | 466.615 | 423.4563 | 413.2254 | 405.2399
BLD3NEW |  |  | Apr | 644.2826 | 620.1771 | 572.6198 | 587.1042 | 491.1385 | 496.5511 | 436.8295 | 590.6829 | 434.2784 | 446.1424 | 534.4977 | 432.9984 | 560.7413 | 424.1977 | 465.9686 | 396.9298
BLD3NEW |  |  | May | 646.3389 | 624.2053 | 577.1864 | 590.4605 | 486.7536 | 497.6449 | 437.5747 | 594.1452 | 432.9063 | 446.9511 | 593.9607 | 433.0368 | 575.8101 | 423.6094 | 514.8917 | 393.4339
BLD3NEW |  |  | Jun | 640.2379 | 613.7647 | 581.4705 | 594.0712 | 487.6928 | 500.1701 | 437.1849 | 593.2967 | 432.7216 | 446.4078 | 599.2377 | 433.1035 | 574.2631 | 406.992 | 517.2153 | 392.5875
BLD3NEW |  |  | Jul | 626.5618 | 622.3393 | 580.9349 | 587.9404 | 485.506 | 500.4242 | 436.9083 | 591.6189 | 433.7415 | 446.2849 | 590.8282 | 432.088 | 571.7111 | 419.456 | 515.1119 | 391.7646
BLD3NEW |  |  | Aug | 629.2002 | 617.0342 | 581.8364 | 584.1342 | 484.7037 | 500.113 | 438.4751 | 603.6024 | 433.3151 | 446.4261 | 586.6008 | 432.3562 | 570.6942 | 423.1538 | 518.3865 | 393.088
BLD3NEW |  |  | Sep | 628.7878 | 628.6542 | 579.1133 | 580.1201 | 487.0047 | 497.5958 | 436.5079 | 593.6291 | 432.7388 | 447.1141 | 593.006 | 433.0234 | 568.8663 | 424.6575 | 515.1524 | 409.3343
BLD3NEW |  |  | Oct | 637.1936 | 609.4171 | 572.1209 | 583.2502 | 488.0144 | 494.0548 | 436.7217 | 586.1591 | 434.7496 | 447.0768 | 587.9329 | 432.8263 | 558.0396 | 425.6208 | 499.6727 | 409.2547
BLD3NEW |  |  | Nov | 638.0162 | 612.0028 | 559.6415 | 566.6074 | 487.6302 | 488.0574 | 438.5263 | 579.3866 | 433.4547 | 434.488 | 589.6725 | 432.3572 | 439.7493 | 417.3593 | 421.1187 | 383.9101
BLD3NEW |  |  | Dec | 636.2717 | 613.545 | 556.7659 | 558.6334 | 490.1439 | 487.0945 | 428.634 | 440.1678 | 423.2566 | 395.9596 | 405.1495 | 412.4612 | 388.9802 | 396.1052 | 384.5798 | 378.3607
BLD3NEW |  |  | Time of Peak Electrical Demand
BLD3NEW |  |  | Jan | 04-JAN-20:00 | 18-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:10 | 26-JAN-20:10 | 29-JAN-08:00 | 27-JAN-20:19 | 09-JAN-06:10 | 26-JAN-20:19 | 27-JAN-20:00 | 17-JAN-20:00 | 24-JAN-20:19 | 30-JAN-20:00 | 30-JAN-20:00 | 20-JAN-20:49 | 21-JAN-08:00
BLD3NEW |  |  | Feb | 17-FEB-20:10 | 22-FEB-20:00 | 27-FEB-20:10 | 22-FEB-07:10 | 23-FEB-20:10 | 08-FEB-20:10 | 13-FEB-20:00 | 13-FEB-06:30 | 13-FEB-20:10 | 21-FEB-20:10 | 17-FEB-20:00 | 10-FEB-20:00 | 19-FEB-20:00 | 03-FEB-20:30 | 22-FEB-20:00 | 28-FEB-20:19
BLD3NEW |  |  | Mar | 14-MAR-19:10 | 31-MAR-19:10 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:10 | 22-MAR-19:10 | 29-MAR-19:00 | 09-MAR-20:10 | 16-MAR-19:10 | 28-MAR-19:10 | 31-MAR-18:10 | 27-MAR-19:30 | 19-MAR-19:00 | 29-MAR-19:19 | 22-MAR-19:10 | 29-MAR-19:00
BLD3NEW |  |  | Apr | 19-APR-19:10 | 04-APR-19:10 | 26-APR-19:10 | 13-APR-19:10 | 11-APR-19:10 | 28-APR-19:10 | 27-APR-19:40 | 05-APR-19:10 | 28-APR-19:10 | 14-APR-19:30 | 28-APR-17:19 | 28-APR-19:19 | 16-APR-19:10 | 19-APR-19:19 | 04-APR-17:30 | 28-APR-19:00
BLD3NEW |  |  | May | 05-MAY-19:10 | 11-MAY-19:10 | 19-MAY-19:19 | 26-MAY-19:40 | 08-MAY-19:10 | 31-MAY-19:10 | 03-MAY-19:19 | 05-MAY-19:10 | 08-MAY-19:00 | 01-MAY-19:19 | 04-MAY-19:10 | 12-MAY-19:49 | 15-MAY-19:30 | 10-MAY-19:49 | 31-MAY-19:49 | 12-MAY-19:00
BLD3NEW |  |  | Jun | 02-JUN-19:10 | 14-JUN-19:19 | 26-JUN-19:40 | 12-JUN-19:49 | 29-JUN-19:00 | 21-JUN-19:10 | 08-JUN-19:00 | 05-JUN-19:30 | 12-JUN-19:00 | 08-JUN-19:00 | 15-JUN-19:30 | 01-JUN-19:00 | 22-JUN-19:00 | 15-JUN-19:00 | 15-JUN-19:00 | 07-JUN-19:10
BLD3NEW |  |  | Jul | 24-JUL-19:00 | 28-JUL-19:19 | 10-JUL-19:49 | 11-JUL-19:49 | 10-JUL-19:10 | 06-JUL-19:10 | 06-JUL-19:00 | 19-JUL-19:30 | 12-JUL-19:19 | 12-JUL-19:00 | 17-JUL-19:19 | 10-JUL-19:30 | 03-JUL-19:00 | 31-JUL-19:00 | 28-JUL-19:49 | 05-JUL-19:10
BLD3NEW |  |  | Aug | 04-AUG-19:10 | 11-AUG-19:10 | 23-AUG-19:10 | 29-AUG-19:10 | 23-AUG-19:10 | 01-AUG-19:49 | 02-AUG-19:30 | 18-AUG-19:10 | 24-AUG-19:19 | 16-AUG-19:19 | 01-AUG-19:10 | 23-AUG-19:10 | 15-AUG-19:19 | 23-AUG-19:00 | 23-AUG-19:10 | 31-AUG-19:10
BLD3NEW |  |  | Sep | 08-SEP-19:00 | 26-SEP-19:10 | 11-SEP-19:10 | 12-SEP-19:10 | 20-SEP-19:10 | 11-SEP-19:10 | 18-SEP-19:00 | 08-SEP-19:10 | 08-SEP-19:10 | 19-SEP-19:10 | 26-SEP-19:10 | 15-SEP-19:40 | 13-SEP-19:10 | 21-SEP-19:10 | 06-SEP-19:10 | 20-SEP-19:10
BLD3NEW |  |  | Oct | 24-OCT-19:10 | 26-OCT-19:10 | 02-OCT-19:10 | 12-OCT-19:10 | 20-OCT-19:00 | 06-OCT-19:10 | 25-OCT-19:00 | 20-OCT-19:10 | 04-OCT-19:10 | 05-OCT-19:10 | 11-OCT-19:10 | 02-OCT-19:10 | 08-OCT-19:10 | 23-OCT-19:10 | 07-OCT-19:10 | 03-OCT-19:00
BLD3NEW |  |  | Nov | 16-NOV-20:10 | 24-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 20-NOV-20:10 | 21-NOV-20:10 | 16-NOV-20:10 | 03-NOV-19:10 | 10-NOV-20:10 | 03-NOV-19:00 | 02-NOV-19:10 | 03-NOV-19:10 | 02-NOV-17:19 | 20-NOV-20:00 | 02-NOV-19:00 | 14-NOV-07:00
BLD3NEW |  |  | Dec | 28-DEC-20:10 | 20-DEC-20:40 | 13-DEC-20:00 | 04-DEC-20:00 | 29-DEC-20:10 | 05-DEC-20:10 | 17-DEC-20:10 | 05-DEC-06:19 | 05-DEC-20:19 | 31-DEC-20:00 | 11-DEC-20:00 | 22-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 18-DEC-07:00
BLD3NEW |  | Source Energy
BLD3NEW |  |  | Total Source Energy (GJ) | 54797.58 | 53957.92 | 44496.03 | 47490.89 | 39800.36 | 44961.07 | 36744.07 | 48900.03 | 39782.65 | 25908.62 | 47819.36 | 40478.67 | 47252.08 | 42440.74 | 46305.32 | 47624.16
BLD3NEW |  |  | Total Source Energy (MJ/m2) | 4829.99 | 4755.98 | 3921.98 | 4185.96 | 3508.1 | 3962.97 | 3238.71 | 4310.16 | 3506.54 | 2283.65 | 4214.91 | 3567.88 | 4164.91 | 3740.83 | 4081.46 | 4197.7
BLD3NEW |  | Water Consumption (m3)
BLD3NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
BLD3NEW |  |  | Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
BLD3NEW |  | Emissions
BLD3NEW |  |  | Carbon Equivalent (kg) | 1221980 | 1309840 | 1114830 | 1127150 | 464798.684 | 1104560 | 441122.5811 | 976691.4578 | 1183200 | 354773.7539 | 1679220 | 1176990 | 1148210 | 1065140 | 1098050 | 931252.8437
BLD3NEW |  |  | CO2 (kg) | 2883200 | 3333260 | 2679280 | 2650860 | 1269400 | 2681060 | 1211230 | 2306320 | 2849550 | 936031.416 | 3995410 | 2850740 | 2784520 | 2605130 | 2689610 | 2463810
BLD3NEW |  |  | NOX (kg) | 4853.6503 | 4237.5164 | 4286.4851 | 4676.6815 | 1105.8505 | 4133.1559 | 1059.5255 | 4045.2729 | 4594.6385 | 1137.3449 | 6726.7476 | 4528.1721 | 4457.5117 | 4056.1552 | 4190.3114 | 2746.8341
BLD3NEW |  |  | SO2 (kg) | 17614.3262 | 16982.7807 | 13426.0968 | 11141.5727 | 8344.102 | 15984.1617 | 7182.9655 | 10786.8198 | 10880.9145 | 1840.7801 | 18600.8549 | 10515.3079 | 6297.1926 | 6129.0334 | 5707.2163 | 10682.6913
BLD3NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD3NEW |  |  | Hg (kg) | 0.0808 | 0.0485 | 0.0371 | 0.0415 | 0.0045 | 0.0307 | 0.0041 | 0.0445 | 0.0434 | 0.0083 | 0.0573 | 0.0421 | 0.0473 | 0.0438 | 0.0432 | 0.0382
BLD3NEW |  |  | Water for Electricity (m3) | 2179.84 | 5792.46 | 99166.1 | 19814.7 | 50335.4 | 79708.2 | 43327.2 | 670.7232 | 11311.9 | 24296.6 | 4281.42 | 10931.3 | 4137.13 | 145321 | 3748.97 | 2143.08

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
| Sun |  |  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
| Sat |  |  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
| Sun |  |  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
| Sat |  |  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
| Sun |  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
[5 empty] | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
[5 empty] | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
[5 empty] | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  | Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
[5 empty] | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
[5 empty] | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
SchGas | WD | Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
| Sat |  |  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
| Sun |  |  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
|  | LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
[5 empty] | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
|  | CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 618 | 4326 | 225570
|  | HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469 | 3283 | 171185
|  | Corr_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
|  | Corr_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
SetCool | All | Guest_CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
SetHeat | All | Guest_HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
|  | Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652 | 4564 | 237980
|  | Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435 | 3045 | 158775
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | HVACOperationSchd | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
|  | MinOA_Sched | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
|  | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
|  | HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
|  | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
|  | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
|  | Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
[5 empty] | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
|  | Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
|  | Kitchen_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
[5 empty] | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
[5 empty] | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
SchSWH | WD | GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
| Sat |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
| Sun |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
|  | LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
|  | Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | Guest Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Guest Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600