## 1
1 | Building Summary Outpatient Health Care pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 3804.01 | 3804.01 | 3804.01
nFloor |  | Number of Floors | 3 | 3 | 3
glazing |  | Total | 0.1985 | 0.1985 | 0.1985
hCeiling |  | Floor to Ceiling Height (m) | 3.05 | 3.05 | 3.05
areaWall |  | Gross Dimensions - Total Area (m2) | 1553.34 | 1553.34 | 1553.34
ver2hor |  | Wall to Skin Ratio | 0.53076 | 0.53076 | 0.53076
areaRoof |  | Gross Dimensions - Total Area (m2) | 1373.29 | 1373.29 | 1373.29
areaWindow |  | Total Area (m2) | 308.29 | 308.29 | 308.29

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BDL7PRE | Total | Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164 | 18.8747 | 23.7788 | 3.2068 | 113.562 | 10 | 1.3186 |  |  | 0.76757
BDL7PRE | Total | Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164 | 18.8747 | 23.7788 | 3.2068 | 113.562 | 10 | 1.3186 |  |  | 0.76757
BDL7PRE | Total | Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164 | 13.4983 | 23.7788 | 3.2068 | 113.562 | 10 | 1.3186 |  |  | 0.20468

## 3
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD7PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD7PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD7PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD7PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD7PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD7PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD7PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD7PRE | HVAC |  | Air Conditioning (kW) | 610.8426 | 625.9154 | 633.9362 | 604.4442 | 481.709 | 573.3666 | 439.7954 | 592.7892 | 505.3798 | 462.572 | 554.7751 | 460.1326 | 533.6079 | 437.7011 | 460.9973 | 387.6273
BLD7PRE | HEAT |  | HEATSYS1 BOILER | 138.0095 | 138.3947 | 131.2853 | 140.2477 | 129.0934 | 128.3124 | 128.8264 | 143.9956 | 125.9352 | 134.3732 | 148.0501 | 130.6299 | 154.1922 | 144.5644 | 152.2497 | 173.9062
BLD7PRE | COP |  | Air Conditioning (COP) | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.0561 | 3.01 | 3.01 | 3.0553 | 3.01 | 3.0582 | 3.01 | 3.0587 | 3.0572 | 3.11
BLD7PRE | EffHeat |  | HEATSYS1 BOILER | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
BLD7PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 27.65 | 28.47 | 30.76 | 29.3 | 26.76 | 30.88 | 26.43 | 27.83 | 30.53 | 27.34 | 25.66 | 27.8 | 25.27 | 26.44 | 24.14 | 23.41
BDL7PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BDL7PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BDL7PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BDL7PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BDL7PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BDL7PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BDL7PST | HVAC |  | Air Conditioning (kW) | 616.0277 | 574.513 | 581.4893 | 545.2917 | 469.4937 | 512.6577 | 397.2252 | 529.7863 | 447.0554 | 414.9117 | 528.8816 | 430.489 | 508.3226 | 413.0393 | 448.0943 | 391.9223
BDL7PST | HEAT |  | HEATSYS1 BOILER | 135.6875 | 131.4663 | 127.2951 | 132.1069 | 126.3248 | 121.191 | 121.3352 | 135.6571 | 120.4736 | 126.737 | 145.764 | 128.8369 | 151.4411 | 142.1619 | 151.5431 | 174.2775
BDL7PST | COP |  | AHU-1_COOLC DXCOIL | 2.73 | 2.73 | 2.73 | 2.73 | 2.7627 | 2.73 | 2.8 | 2.73 | 2.7643 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.7637 | 2.8
BDL7PST | EffHeat |  | HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BDL7PST | Fan |  | Fan Max Flow Rate (m3/s ) | 28.04 | 25.24 | 27.42 | 25.49 | 25.92 | 26.68 | 23.67 | 23.91 | 27.01 | 24.05 | 24.05 | 26.01 | 23.59 | 24.95 | 23.2 | 23.68
BDL7NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BDL7NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BDL7NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BDL7NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BDL7NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BDL7NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BDL7NEW | HVAC |  | Air Conditioning (kW) | 498.5725 | 504.5554 | 502.518 | 476.8165 | 382.0583 | 443.7767 | 362.9994 | 480.54 | 408.643 | 374.4653 | 472.8985 | 396.384 | 461.1064 | 382.7874 | 411.7201 | 319.6834
BDL7NEW | HEAT |  | HEATSYS1 BOILER | 124.739 | 125.1364 | 115.3736 | 124.9673 | 115.0652 | 113.5958 | 117.9526 | 130.357 | 114.6396 | 122.5312 | 139.2338 | 122.7386 | 143.0675 | 133.9838 | 143.2942 | 159.0514
BDL7NEW | COP |  | AHU-1_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.1754 | 3.23 | 3.13 | 3.23 | 3.23 | 3.177 | 3.23 | 3.1773 | 3.23 | 3.23 | 3.23
BDL7NEW | EffHeat |  | HEATSYS1 BOILER | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
BDL7NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 21.9 | 22.25 | 23.48 | 22.25 | 20.62 | 22.98 | 21.61 | 22.05 | 24.69 | 21.62 | 21.77 | 23.94 | 21.83 | 23.12 | 21.67 | 19.31
Note on E12: Joseph Yang: ?? Incorrect?

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
| Sun |  |  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
| Sun |  |  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
| Sat |  |  |  | Sat, WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
| Sun |  |  |  | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
| Sat |  |  |  | Sat, WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
| Sun |  |  |  | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
SchGas | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.83 | 41.88 | 2183.74
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.49
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24
SchSWH | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
| Sat |  |  |  | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| Sun |  |  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01

## BuildingSummary
1 | Building Summary Outpatient Health Care pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Outpatient Health Care Reference Building pre-1980 construction | Outpatient Health Care Reference Building post-1980 construction | Outpatient Health Care Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Health care, outpatient | Health care, outpatient | Health care, outpatient
Form
areaFloor |  | Total Floor Area (m2) | 3804.01 | 3804.01 | 3804.01
|  | Building Shape | Irregular | Irregular | Irregular
|  | Aspect Ratio | 1.43 | 1.43 | 1.43
nFloor |  | Number of Floors | 3 | 3 | 3
Window Fraction (Window to Wall Ratio)
|  | South | 0.2408 | 0.2408 | 0.2408
|  | East | 0.1914 | 0.1914 | 0.1914
|  | North | 0.2052 | 0.2052 | 0.2052
|  | West | 0.1288 | 0.1288 | 0.1288
glazing |  | Total | 0.1985 | 0.1985 | 0.1985
|  | Skylight/TDD Percentage | 0 | 0 | 0
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | Zoned By Use | Zoned By Use | Zoned By Use
hCeiling |  | Floor to Ceiling Height (m) | 3.05 | 3.05 | 3.05
|  | Floor to Floor Height (m) | 3.05 | 3.05 | 3.05
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Steel frame | Steel frame | Steel frame
areaWall |  | Gross Dimensions - Total Area (m2) | 1553.34 | 1553.34 | 1553.34
|  | Net Dimensions - Total Area (m2) | 1245.05 | 1245.05 | 1245.05
ver2hor |  | Wall to Skin Ratio | 0.53076 | 0.53076 | 0.53076
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 1373.29 | 1373.29 | 1373.29
|  | Net Dimensions - Total Area (m2) | 1373.29 | 1373.29 | 1373.29
|  | Roof to Skin Ratio | 0.46924 | 0.46924 | 0.46924
Window Dimensions (m2)
|  | South | 114.08 | 114.08 | 114.08
|  | East | 57.97 | 57.97 | 57.97
|  | North | 97.22 | 97.22 | 97.22
|  | West | 39.02 | 39.02 | 39.02
areaWindow |  | Total Area (m2) | 308.29 | 308.29 | 308.29
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
|  | Dimensions - Total Area (m2) | 1373.29 | 1373.29 | 1373.29
Interior Partitions
|  | Construction | Gypsum Board | Gypsum Board | Gypsum Board
Dimensions - Total Area (m2)
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 2746.58 | 2746.58 | 2746.58
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ft3/min per ft2 of exterior wall) | 0.93401 | 0.93401 | 0.27988
HVAC
|  | System Type | Packaged VAV With Reheat | Packaged VAV With Reheat | Packaged VAV With Reheat
|  | Heating Type | Hot Water Boiler, Furnace | Hot Water Boiler, Furnace | Hot Water Boiler, Furnace
|  | Cooling Type | DX Cooling Coil | DX Cooling Coil | DX Cooling Coil
|  | Fan Control | VAV | VAV | VAV
Service Water Heating
|  | SWH Type | Gas Water Heater | Gas Water Heater | Gas Water Heater
|  | Fuel | Gas | Gas | Gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 240.48 | 240.48 | 240.48

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 22.6042 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 1.1157 | 11.1943
|  | Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0 | 0
|  | Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 13.9931 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.63761 | 24.8792
|  | Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 13.9931 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0 | 0
|  | Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 13.9931 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0 | 0
|  | Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 19.375 | 11.84 |  |  | 10 |  | 5.8529 |  | 0 | 0
|  | Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 19.375 | 11.84 |  |  | 10 |  | 2.0903 |  | 2.6777 | 11.1943
|  | Floor 1 Electrical Room | No | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 7.5347 | 53.82 | [6 empty] | 0.95598
|  | Floor 1 Elevator Pump Room | No | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 7.5347 | 529.29 | [6 empty] | 2.9428
|  | Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 19.375 | 11.84 |  |  | 10 |  | 2.5084 |  | 0 | 0
|  | Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0 | 0
|  | Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 19.375 | 11.84 |  |  | 10 |  | 5.2026 |  | 0 | 0
|  | Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 10.7639 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.47364 | 27.3698
|  | Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0 | 0
|  | Floor 1 Lobby Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
|  | Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 9.6875 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.44637 | 27.3698
|  | Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0 | 0
|  | Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 9.6875 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0 | 0
|  | Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 4.9269 | 25.6325
|  | Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 22.6042 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.39894 | 6.2265
|  | Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0 | 0
|  | Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 22.6042 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0 | 0
|  | Floor 1 MRI Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
|  | Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 22.6042 | 21.53 |  |  | 10 |  | 33.8167 |  | 0 | 0
|  | Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0 | 0
|  | Floor 1 Nurse Janitor | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 22.6042 | 21.53 |  |  | 10 |  | 48.4954 |  | 0 | 0
|  | Floor 1 Nurse Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 0
|  | Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 19.375 | 11.84 |  |  | 10 |  | 22.4361 |  | 0 | 0
|  | Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 1.2518 | 53.4944
|  | Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.66961 | 29.8604
|  | Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0 | 0
|  | Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 24.757 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0 | 0
|  | Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0 | 0
|  | Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 15.0695 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.28369 | 4.9812
|  | Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 15.0695 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0 | 0
|  | Floor 1 Pre-Op Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
|  | Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 17.2222 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.89261 | 23.6339
|  | Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 10.7639 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.34207 | 16.1755
|  | Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0 | 0
|  | Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 24.757 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 1.116 | 55.985
|  | Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 19.375 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.78728 | 8.7037
|  | Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0 | 0
|  | Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 9.6875 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0 | 0
|  | Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 9.6875 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0 | 0
|  | Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 9.6875 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0 | 0
|  | Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 24.757 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 1.6513 | 46.0226
|  | Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.17385 | 9.949
|  | Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0 | 0
|  | Floor 1 Storage | No | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 10.7639 | 0 | [6 empty] | 2.256
|  | Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.95671 | 17.4208
|  | Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.83664 | 19.898
|  | Floor 1 Utility Janitor | No | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 1 Utility Room | No | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 2.0084
|  | Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 1.4874 | 9.949
|  | Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 19.375 | 10.76 |  |  | 10 |  | 156.0771 |  | 1.594 | 49.7585
|  | Floor 2 Conference Toilet | No | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 50.3426 | 0
|  | Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 19.375 | 11.84 |  |  | 10 |  | 3.2516 |  | 0 | 0
|  | Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 17.2222 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 1.5622 | 52.2491
|  | Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 17.2222 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.44628 | 22.3886
|  | Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 17.2222 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.44641 | 29.8604
|  | Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 17.2222 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 1.1153 | 8.7037
|  | Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 17.2222 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.95663 | 31.1057
|  | Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 17.2222 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.89298 | 18.6661
|  | Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 17.2222 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.40583 | 29.8604
|  | Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 17.2222 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.89255 | 22.3886
|  | Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 17.2222 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.40583 | 14.9302
|  | Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601 | 7.4584
|  | Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601 | 7.4584
|  | Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601 | 7.4584
|  | Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546 | 7.4584
|  | Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546 | 7.4584
|  | Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546 | 7.4584
|  | Floor 2 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 3.3997
|  | Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 9.6875 | 32.29 |  |  | 8 |  | 8.9187 |  | 0 | 0
|  | Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 22.6042 | 21.53 |  |  | 10 |  | 27.8709 |  | 0 | 0
|  | Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 22.6042 | 21.53 |  |  | 10 |  | 33.4451 |  | 0 | 0
|  | Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 19.375 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.95642 | 49.7585
|  | Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0 | 0
|  | Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 10.7639 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.66676 | 60.9528
|  | Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 2.2318 | 116.9377
|  | Floor 2 Reception Toilet | No | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 99.1089 | 0
|  | Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 19.375 | 11.84 |  |  | 10 |  | 15.0503 |  | 0 | 0
|  | Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 19.375 | 11.84 |  |  | 10 |  | 15.8864 |  | 0 | 0
|  | Floor 2 Storage 1 | No | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 2 Storage 2 | No | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 2 Storage 3 | No | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 2 Utility | No | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 0.95631
|  | Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 19.375 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.20596 | 32.3376
|  | Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.096261 | 7.4584
|  | Floor 2 Work Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
|  | Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 22.6042 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0 | 0
|  | Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 19.375 | 11.84 |  |  | 10 |  | 1.951 |  | 1.339 | 5.2248
|  | Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 1.4839 | 51.0092
|  | Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 19.375 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 1.339 | 13.4352
|  | Floor 3 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 4.7387
|  | Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 9.6875 | 32.29 |  |  | 8 |  | 13.378 |  | 1.339 | 14.928
|  | Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 9.6875 | 32.29 |  |  | 8 |  | 84.6161 |  | 1.7448 | 123.0348
|  | Floor 3 Lounge Toilet | No | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 8.6111 | 4.31 | [5 empty] | 151.023 | 2.1761
|  | Floor 3 Mechanical | No | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 7.5347 | 53.82 | [6 empty] | 2.2957
|  | Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 1.339 | 37.32
|  | Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 19.375 | 11.84 |  |  | 10 |  | 141.0268 |  | 1.6654 | 469.7373
|  | Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 1.4353 | 111.2081
|  | Floor 3 Office Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 2.8257
|  | Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 2.2146 | 267.4636
|  | Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 1.339 | 73.6449
|  | Floor 3 Physical Therapy Toilet | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 66.0726 | 1.339
|  | Floor 3 Storage 1 | No | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
|  | Floor 3 Storage 2 | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
|  | Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 17.2222 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 1.339 | 59.2145
|  | Floor 3 Undeveloped 1 | No | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 |  | 0 | 0 | 0 | [6 empty] | 1.7641
|  | Floor 3 Undeveloped 2 | No | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 |  | 0 | 0 | 0 | [6 empty] | 1.99
|  | Floor 3 Utility | No | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 | [6 empty] | 1.339
|  | Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 19.375 | 11.84 |  |  | 10 |  | 26.6632 |  | 2.2955 | 122.4094
|  | NE Stair | No | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 8.6111 | 0 | [6 empty] | 1
|  | NW Elevator | No | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 1
|  | NW Stair | No | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 8.6111 | 0 | [6 empty] | 1
|  | SW Stair | No | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 8.6111 | 0 | [6 empty] | 1
BDL7PRE | Total | Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164 | 18.8747 | 23.7788 | 3.2068 | 113.562 |  | 1.3186 | 4072.5401 |  | 0.76757
|  | Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 22.6042 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 1.1157 | 11.1943
|  | Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0 | 0
|  | Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 13.9931 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.63761 | 24.8792
|  | Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 13.9931 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0 | 0
|  | Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 13.9931 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0 | 0
|  | Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 19.375 | 11.84 |  |  | 10 |  | 5.8529 |  | 0 | 0
|  | Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 19.375 | 11.84 |  |  | 10 |  | 2.0903 |  | 2.6777 | 11.1943
|  | Floor 1 Electrical Room | No | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 7.5347 | 53.82 | [6 empty] | 0.95598
|  | Floor 1 Elevator Pump Room | No | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 7.5347 | 529.29 | [6 empty] | 2.9428
|  | Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 19.375 | 11.84 |  |  | 10 |  | 2.5084 |  | 0 | 0
|  | Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0 | 0
|  | Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 19.375 | 11.84 |  |  | 10 |  | 5.2026 |  | 0 | 0
|  | Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 10.7639 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.47364 | 27.3698
|  | Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0 | 0
|  | Floor 1 Lobby Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
|  | Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 9.6875 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.44637 | 27.3698
|  | Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0 | 0
|  | Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 9.6875 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0 | 0
|  | Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 4.9269 | 25.6325
|  | Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 22.6042 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.39894 | 6.2265
|  | Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0 | 0
|  | Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 22.6042 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0 | 0
|  | Floor 1 MRI Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
|  | Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 22.6042 | 21.53 |  |  | 10 |  | 33.8167 |  | 0 | 0
|  | Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0 | 0
|  | Floor 1 Nurse Janitor | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 22.6042 | 21.53 |  |  | 10 |  | 48.4954 |  | 0 | 0
|  | Floor 1 Nurse Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 0
|  | Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 19.375 | 11.84 |  |  | 10 |  | 22.4361 |  | 0 | 0
|  | Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 1.2518 | 53.4944
|  | Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.66961 | 29.8604
|  | Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0 | 0
|  | Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 24.757 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0 | 0
|  | Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0 | 0
|  | Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 15.0695 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.28369 | 4.9812
|  | Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 15.0695 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0 | 0
|  | Floor 1 Pre-Op Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
|  | Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 17.2222 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.89261 | 23.6339
|  | Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 10.7639 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.34207 | 16.1755
|  | Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0 | 0
|  | Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 24.757 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 1.116 | 55.985
|  | Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 19.375 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.78728 | 8.7037
|  | Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0 | 0
|  | Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 9.6875 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0 | 0
|  | Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 9.6875 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0 | 0
|  | Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 9.6875 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0 | 0
|  | Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 24.757 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 1.6513 | 46.0226
|  | Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.17385 | 9.949
|  | Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0 | 0
|  | Floor 1 Storage | No | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 10.7639 | 0 | [6 empty] | 2.256
|  | Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.95671 | 17.4208
|  | Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.83664 | 19.898
|  | Floor 1 Utility Janitor | No | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 1 Utility Room | No | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 2.0084
|  | Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 1.4874 | 9.949
|  | Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 19.375 | 10.76 |  |  | 10 |  | 156.0771 |  | 1.594 | 49.7585
|  | Floor 2 Conference Toilet | No | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 50.3426 | 0
|  | Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 19.375 | 11.84 |  |  | 10 |  | 3.2516 |  | 0 | 0
|  | Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 17.2222 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 1.5622 | 52.2491
|  | Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 17.2222 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.44628 | 22.3886
|  | Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 17.2222 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.44641 | 29.8604
|  | Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 17.2222 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 1.1153 | 8.7037
|  | Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 17.2222 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.95663 | 31.1057
|  | Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 17.2222 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.89298 | 18.6661
|  | Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 17.2222 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.40583 | 29.8604
|  | Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 17.2222 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.89255 | 22.3886
|  | Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 17.2222 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.40583 | 14.9302
|  | Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601 | 7.4584
|  | Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601 | 7.4584
|  | Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601 | 7.4584
|  | Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546 | 7.4584
|  | Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546 | 7.4584
|  | Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546 | 7.4584
|  | Floor 2 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 3.3997
|  | Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 9.6875 | 32.29 |  |  | 8 |  | 8.9187 |  | 0 | 0
|  | Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 22.6042 | 21.53 |  |  | 10 |  | 27.8709 |  | 0 | 0
|  | Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 22.6042 | 21.53 |  |  | 10 |  | 33.4451 |  | 0 | 0
|  | Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 19.375 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.95642 | 49.7585
|  | Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0 | 0
|  | Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 10.7639 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.66676 | 60.9528
|  | Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 2.2318 | 116.9377
|  | Floor 2 Reception Toilet | No | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 99.1089 | 0
|  | Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 19.375 | 11.84 |  |  | 10 |  | 15.0503 |  | 0 | 0
|  | Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 19.375 | 11.84 |  |  | 10 |  | 15.8864 |  | 0 | 0
|  | Floor 2 Storage 1 | No | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 2 Storage 2 | No | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 2 Storage 3 | No | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
|  | Floor 2 Utility | No | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 0.95631
|  | Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 19.375 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.20596 | 32.3376
|  | Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.096261 | 7.4584
|  | Floor 2 Work Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
|  | Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 22.6042 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0 | 0
|  | Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 19.375 | 11.84 |  |  | 10 |  | 1.951 |  | 1.339 | 5.2248
|  | Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 1.4839 | 51.0092
|  | Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 19.375 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 1.339 | 13.4352
|  | Floor 3 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 4.7387
|  | Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 9.6875 | 32.29 |  |  | 8 |  | 13.378 |  | 1.339 | 14.928
|  | Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 9.6875 | 32.29 |  |  | 8 |  | 84.6161 |  | 1.7448 | 123.0348
|  | Floor 3 Lounge Toilet | No | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 8.6111 | 4.31 | [5 empty] | 151.023 | 2.1761
|  | Floor 3 Mechanical | No | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 7.5347 | 53.82 | [6 empty] | 2.2957
|  | Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 1.339 | 37.32
|  | Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 19.375 | 11.84 |  |  | 10 |  | 141.0268 |  | 1.6654 | 469.7373
|  | Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 1.4353 | 111.2081
|  | Floor 3 Office Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 2.8257
|  | Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 2.2146 | 267.4636
|  | Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 1.339 | 73.6449
|  | Floor 3 Physical Therapy Toilet | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 66.0726 | 1.339
|  | Floor 3 Storage 1 | No | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
|  | Floor 3 Storage 2 | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
|  | Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 17.2222 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 1.339 | 59.2145
|  | Floor 3 Undeveloped 1 | No | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 |  | 0 | 0 | 0 | [6 empty] | 1.7641
|  | Floor 3 Undeveloped 2 | No | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 |  | 0 | 0 | 0 | [6 empty] | 1.99
|  | Floor 3 Utility | No | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 | [6 empty] | 1.339
|  | Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 19.375 | 11.84 |  |  | 10 |  | 26.6632 |  | 2.2955 | 122.4094
|  | NE Stair | No | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 8.6111 | 0 | [6 empty] | 1
|  | NW Elevator | No | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 1
|  | NW Stair | No | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 8.6111 | 0 | [6 empty] | 1
|  | SW Stair | No | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 8.6111 | 0 | [6 empty] | 1
BDL7PRE | Total | Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 1196.7491 | 18.8747 | 23.7788 | 3.2068 | 113.562 | 10 | 1.3186 | 4072.5401 |  | 0.76757
|  | Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 32.29 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 0.29752 | 2.9852
|  | Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 9.69 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0 | 0
|  | Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 9.69 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.17003 | 6.6345
|  | Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 12.92 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0 | 0
|  | Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 12.92 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0 | 0
|  | Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 11.84 | 11.84 |  |  | 10 |  | 5.8529 |  | 0 | 0
|  | Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 11.84 | 11.84 |  |  | 10 |  | 2.0903 |  | 0.71404 | 2.9852
|  | Floor 1 Electrical Room | No | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 16.15 | 53.82 | [6 empty] | 0.25493
|  | Floor 1 Elevator Pump Room | No | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 16.15 | 529.29 | [6 empty] | 0.78476
|  | Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 11.84 | 11.84 |  |  | 10 |  | 2.5084 |  | 0 | 0
|  | Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0 | 0
|  | Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 11.84 | 11.84 |  |  | 10 |  | 5.2026 |  | 0 | 0
|  | Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 13.99 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.12631 | 7.2986
|  | Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0 | 0
|  | Floor 1 Lobby Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.39645
|  | Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 8.61 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.11903 | 7.2986
|  | Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0 | 0
|  | Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 8.61 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0 | 0
|  | Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 9.69 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 1.3138 | 6.8353
|  | Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 4.31 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.10638 | 1.6604
|  | Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0 | 0
|  | Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 4.31 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0 | 0
|  | Floor 1 MRI Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.39645
|  | Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 10.76 | 21.53 |  |  | 10 |  | 33.8167 |  | 0 | 0
|  | Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0 | 0
|  | Floor 1 Nurse Janitor | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
|  | Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 10.76 | 21.53 |  |  | 10 |  | 48.4954 |  | 0 | 0
|  | Floor 1 Nurse Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0
|  | Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 11.84 | 11.84 |  |  | 10 |  | 22.4361 |  | 0 | 0
|  | Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 23.68 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 0.3338 | 14.2652
|  | Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 23.68 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.17856 | 7.9628
|  | Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 23.68 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0 | 0
|  | Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 8.61 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0 | 0
|  | Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0 | 0
|  | Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 7.53 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.07565 | 1.3283
|  | Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 7.53 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0 | 0
|  | Floor 1 Pre-Op Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.39645
|  | Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 29.06 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.23803 | 6.3024
|  | Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 13.99 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.091218 | 4.3135
|  | Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0 | 0
|  | Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 8.61 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 0.29759 | 14.9293
|  | Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 11.84 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.20994 | 2.321
|  | Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0 | 0
|  | Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 12.92 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0 | 0
|  | Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 12.92 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0 | 0
|  | Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 12.92 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0 | 0
|  | Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 8.61 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 0.44034 | 12.2727
|  | Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.046359 | 2.6531
|  | Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 9.69 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0 | 0
|  | Floor 1 Storage | No | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 9.69 | 0 | [6 empty] | 0.6016
|  | Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.25512 | 4.6456
|  | Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.2231 | 5.3061
|  | Floor 1 Utility Janitor | No | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
|  | Floor 1 Utility Room | No | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 9.69 | 1.08 | [6 empty] | 0.53559
|  | Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 0.39663 | 2.6531
|  | Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 13.99 | 10.76 |  |  | 10 |  | 156.0771 |  | 0.42508 | 13.2689
|  | Floor 2 Conference Toilet | No | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 50.3426 | 0
|  | Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 11.84 | 11.84 |  |  | 10 |  | 3.2516 |  | 0 | 0
|  | Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 16.15 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 0.4166 | 13.9331
|  | Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 16.15 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.11901 | 5.9703
|  | Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 16.15 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.11904 | 7.9628
|  | Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 16.15 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 0.29742 | 2.321
|  | Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 16.15 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.2551 | 8.2949
|  | Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 16.15 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.23813 | 4.9776
|  | Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 16.15 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.10822 | 7.9628
|  | Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 16.15 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.23801 | 5.9703
|  | Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 16.15 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.10822 | 3.9814
|  | Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.11894 | 1.9889
|  | Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.11894 | 1.9889
|  | Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.11894 | 1.9889
|  | Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.10812 | 1.9889
|  | Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.10812 | 1.9889
|  | Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.10812 | 1.9889
|  | Floor 2 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0.90658
|  | Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 8.61 | 32.29 |  |  | 8 |  | 8.9187 |  | 0 | 0
|  | Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 10.76 | 21.53 |  |  | 10 |  | 27.8709 |  | 0 | 0
|  | Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 10.76 | 21.53 |  |  | 10 |  | 33.4451 |  | 0 | 0
|  | Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 11.84 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.25505 | 13.2689
|  | Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0 | 0
|  | Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 13.99 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.1778 | 16.2541
|  | Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 0.59513 | 31.1834
|  | Floor 2 Reception Toilet | No | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 99.1089 | 0
|  | Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 11.84 | 11.84 |  |  | 10 |  | 15.0503 |  | 0 | 0
|  | Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 11.84 | 11.84 |  |  | 10 |  | 15.8864 |  | 0 | 0
|  | Floor 2 Storage 1 | No | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
|  | Floor 2 Storage 2 | No | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
|  | Floor 2 Storage 3 | No | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0
|  | Floor 2 Utility | No | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 9.69 | 1.08 | [6 empty] | 0.25502
|  | Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 11.84 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.054924 | 8.6234
|  | Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.02567 | 1.9889
|  | Floor 2 Work Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 0.39645
|  | Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 4.31 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0 | 0
|  | Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 11.84 | 11.84 |  |  | 10 |  | 1.951 |  | 0.35708 | 1.3933
|  | Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 0.39572 | 13.6025
|  | Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 11.84 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 0.35708 | 3.5827
|  | Floor 3 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 1.2637
|  | Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 8.61 | 32.29 |  |  | 8 |  | 13.378 |  | 0.35708 | 3.9808
|  | Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 8.61 | 32.29 |  |  | 8 |  | 84.6161 |  | 0.46529 | 32.8093
|  | Floor 3 Lounge Toilet | No | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 9.69 | 4.31 | [5 empty] | 151.023 | 0.58028
|  | Floor 3 Mechanical | No | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 16.15 | 53.82 | [6 empty] | 0.61218
|  | Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 0.35708 | 9.952
|  | Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 11.84 | 11.84 |  |  | 10 |  | 141.0268 |  | 0.44411 | 125.2633
|  | Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 10.76 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.38274 | 29.6555
|  | Floor 3 Office Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 42.4752 | 0.75353
|  | Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 9.69 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 0.59055 | 71.3236
|  | Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 9.69 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 0.35708 | 19.6386
|  | Floor 3 Physical Therapy Toilet | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 9.69 | 4.31 | [5 empty] | 66.0726 | 0.35708
|  | Floor 3 Storage 1 | No | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0.35708
|  | Floor 3 Storage 2 | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 9.69 | 0 | [6 empty] | 0.35708
|  | Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 16.15 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 0.35708 | 15.7905
|  | Floor 3 Undeveloped 1 | No | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 |  | 0 | 0 | 0 | [6 empty] | 0.47043
|  | Floor 3 Undeveloped 2 | No | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 |  | 0 | 0 | 0 | [6 empty] | 0.53067
|  | Floor 3 Utility | No | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 9.69 | 1.08 | [6 empty] | 0.35708
|  | Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 11.84 | 11.84 |  |  | 10 |  | 26.6632 |  | 0.61213 | 32.6425
|  | NE Stair | No | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 10.76 | 0 | [6 empty] | 1
|  | NW Elevator | No | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 10.76 | 0 | [6 empty] | 1
|  | NW Stair | No | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 10.76 | 0 | [6 empty] | 1
|  | SW Stair | No | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 10.76 | 0 | [6 empty] | 1
BDL7PRE | Total | Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164 | 13.4983 | 23.7788 | 3.2068 | 113.562 |  | 1.3186 | 4072.5401 |  | 0.20468

## LocationSummary
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD7PRE |  | Program
BLD7PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD7PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD7PRE |  |  | Weighting Factor
BLD7PRE |  | Fabric
BLD7PRE |  |  | Exterior walls
BLD7PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD7PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD7PRE |  |  | Roof
BLD7PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD7PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD7PRE |  |  | Window
BLD7PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD7PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD7PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD7PRE |  |  | Skylights/TDD
BLD7PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD7PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD7PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD7PRE |  |  | Foundation
BLD7PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD7PRE |  |  | Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
BLD7PRE |  |  | R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
BLD7PRE |  | HVAC
BLD7PRE |  |  | HVAC Sizing
BLD7PRE | HVAC |  | Air Conditioning (kW) | 610.8426 | 625.9154 | 633.9362 | 604.4442 | 481.709 | 573.3666 | 439.7954 | 592.7892 | 505.3798 | 462.572 | 554.7751 | 460.1326 | 533.6079 | 437.7011 | 460.9973 | 387.6273
BLD7PRE |  |  | AHU-1_COOLC DXCOIL | 280.9098 | 282.282 | 275.6667 | 272.8685 | 223.52 | 247.8325 | 202.8277 | 269.3367 | 236.622 | 209.6443 | 257.2825 | 221.6156 | 251.1956 | 213.3376 | 217.5178 | 186.287
BLD7PRE |  |  | AHU-2_COOLC DXCOIL | 329.9329 | 343.6334 | 358.2695 | 331.5756 | 258.189 | 325.5341 | 236.9677 | 323.4525 | 268.7578 | 252.9276 | 297.4926 | 238.5169 | 282.4123 | 224.3634 | 243.4795 | 201.3402
BLD7PRE |  |  | Heating (kW)
BLD7PRE | HEAT |  | HEATSYS1 BOILER | 138.0095 | 138.3947 | 131.2853 | 140.2477 | 129.0934 | 128.3124 | 128.8264 | 143.9956 | 125.9352 | 134.3732 | 148.0501 | 130.6299 | 154.1922 | 144.5644 | 152.2497 | 173.9062
BLD7PRE |  |  | HVAC Efficiency
BLD7PRE | COP |  | Air Conditioning (COP) | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.0561 | 3.01 | 3.01 | 3.0553 | 3.01 | 3.0582 | 3.01 | 3.0587 | 3.0572 | 3.11
BLD7PRE |  |  | AHU-1_COOLC DXCOIL | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.11 | 3.01 | 3.01 | 3.11 | 3.01 | 3.11 | 3.01 | 3.11 | 3.11 | 3.11
BLD7PRE |  |  | AHU-2_COOLC DXCOIL | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.11
BLD7PRE |  |  | Heating Efficiency (%)
BLD7PRE | EffHeat |  | HEATSYS1 BOILER | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
BLD7PRE |  |  | HVAC Control - Economizer
BLD7PRE |  |  | AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD7PRE |  |  | AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD7PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 27.65 | 28.47 | 30.76 | 29.3 | 26.76 | 30.88 | 26.43 | 27.83 | 30.53 | 27.34 | 25.66 | 27.8 | 25.27 | 26.44 | 24.14 | 23.41
BLD7PRE |  |  | AHU-1_FAN | 12.91 | 13.07 | 13.49 | 13.44 | 12.7 | 13.63 | 12.25 | 12.92 | 14.29 | 12.66 | 12.19 | 13.39 | 12.24 | 12.89 | 11.73 | 11.25
BLD7PRE |  |  | AHU-2_FAN | 14.74 | 15.4 | 17.27 | 15.86 | 14.06 | 17.25 | 14.18 | 14.91 | 16.24 | 14.68 | 13.47 | 14.41 | 13.03 | 13.55 | 12.41 | 12.16
BLD7PRE |  | Utility Costs
BLD7PRE |  |  | Electric Utility Rates
BLD7PRE |  |  | Average Annual Rate ($/kWh) | 0.080254 | 0.10635 | 0.078191 | 0.098843 | 0.12314 | 0.091364 | 0.14403 | 0.068551 | 0.037037 | 0.071511 | 0.09697 | 0.037044 | 0.054177 | 0.071339 | 0.054073 | 0.090907
BLD7PRE |  |  | Total Cost ($/m2) | 38.88 | 50.28 | 38.55 | 45.59 | 50.67 | 45.44 | 54.94 | 31.15 | 17.2 | 28.53 | 41.22 | 16.1 | 23.19 | 30.17 | 22.38 | 39.49
BLD7PRE |  |  | Gas Utility Rates
BLD7PRE |  |  | Average Annual Rate ($/MJ) | 0.011409 | 0.0081555 | 0.008585 | 0.010782 | 0.0083905 | 0.0081271 | 0.0083897 | 0.010099 | 0.0072206 | 0.0082733 | 0.0089745 | 0.0072283 | 0.0079809 | 0.0088442 | 0.00799 | 0.004192
BLD7PRE |  |  | Total Cost ($/m2) | 8.35 | 7.14 | 7.89 | 10.9 | 8.42 | 7.42 | 8.81 | 10.67 | 6.75 | 9.19 | 9.35 | 6.67 | 8.76 | 8.99 | 8.84 | 5.65
BLD7PRE |  |  | Total Utility Costs
BLD7PRE |  |  | Cost Intensity ($/m2) | 47.23 | 57.42 | 46.44 | 56.49 | 59.09 | 52.86 | 63.76 | 41.82 | 23.95 | 37.72 | 50.57 | 22.77 | 31.94 | 39.15 | 31.22 | 45.15
BLD7PRE |  | Energy - End Uses
BLD7PRE |  |  | Electricity (kWh)
BLD7PRE |  |  | Heating | 10488.8889 | 51900 | 46827.7778 | 87505.5556 | 37244.4444 | 62791.6667 | 74513.8889 | 118747.2222 | 79363.8889 | 128650 | 116086.1111 | 84030.5556 | 130888.8889 | 111300 | 153500 | 235941.6667
BLD7PRE |  |  | Cooling | 742988.8889 | 634663.8889 | 634947.2222 | 505519.4444 | 427300 | 527572.2222 | 296772.2222 | 423544.4444 | 371161.1111 | 270733.3333 | 316841.6667 | 279497.2222 | 282172.2222 | 225136.1111 | 186372.2222 | 129761.1111
BLD7PRE |  |  | Interior Lighting | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667
BLD7PRE |  |  | Exterior Lighting | 74091.6667 | 74063.8889 | 74050 | 74038.8889 | 73983.3333 | 73966.6667 | 74005.5556 | 73961.1111 | 73988.8889 | 73841.6667 | 73972.2222 | 73927.7778 | 73922.2222 | 73905.5556 | 73863.8889 | 73411.1111
BLD7PRE |  |  | Interior Equipment | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778
BLD7PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans | 287047.2222 | 288325 | 303288.8889 | 295030.5556 | 277175 | 306347.2222 | 266800 | 281633.3333 | 316463.8889 | 275352.7778 | 265072.2222 | 292452.7778 | 265647.2222 | 280030.5556 | 254558.3333 | 243722.2222
BLD7PRE |  |  | Pumps | 6038.8889 | 6052.7778 | 5738.8889 | 6136.1111 | 5650 | 5583.3333 | 5638.8889 | 6272.2222 | 5513.8889 | 5875 | 6466.6667 | 5716.6667 | 6727.7778 | 6319.4444 | 6647.2222 | 7544.4444
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 1536.1111 | 22725 | 89833.3333 | 65538.8889 | 22986.1111 | 194933.3333 | 12580.5556 | 103588.8889 | 199313.8889 | 42427.7778 | 117758.3333 | 196544.4444 | 147986.1111 | 191061.1111 | 178425 | 241405.5556
BLD7PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 1842983.3333 | 1798525 | 1875477.7778 | 1754561.1111 | 1565133.3333 | 1891986.1111 | 1451105.5556 | 1728538.8889 | 1766597.2222 | 1517675 | 1616988.8889 | 1652963.8889 | 1628138.8889 | 1608547.2222 | 1574163.8889 | 1652580.5556
BLD7PRE |  |  | Gas (MJ)
BLD7PRE |  |  | Heating | 2568370 | 3106260 | 3277480 | 3619520 | 3592270 | 3252010 | 3765570 | 3789350 | 3326410 | 3991910 | 3728910 | 3277490 | 3935530 | 3626140 | 3966430 | 4880280
BLD7PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
BLD7PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems | 28110 | 33520 | 30380 | 38750 | 37740 | 34120 | 42220 | 42850 | 42060 | 44990 | 46480 | 46290 | 49570 | 50170 | 54750 | 60970
BLD7PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 2784850 | 3328150 | 3496230 | 3846650 | 3818390 | 3474510 | 3996160 | 4020580 | 3556840 | 4225280 | 3963760 | 3512150 | 4173480 | 3864680 | 4209550 | 5129630
BLD7PRE |  |  | Purchased Cooling (MJ)
BLD7PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Purchased Heating (MJ)
BLD7PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total Building (MJ) | 9419590 | 9802840 | 10247960 | 10163070 | 9452870 | 10285660 | 9220140 | 10243310 | 9916590 | 9688910 | 9784930 | 9462820 | 10034780 | 9655450 | 9876540 | 11078930
BLD7PRE |  | Energy - End Use Intensities
BLD7PRE |  |  | Electricity (MJ/m2)
BLD7PRE |  |  | Heating (elec) | 9.9264 | 49.1166 | 44.3164 | 82.8126 | 35.247 | 59.4241 | 70.5177 | 112.3788 | 75.1076 | 121.7505 | 109.8604 | 79.524 | 123.8693 | 105.331 | 145.2678 | 223.2881
BLD7PRE |  |  | Cooling (elec) | 703.1422 | 600.6267 | 600.8948 | 478.4083 | 404.3838 | 499.2784 | 280.8563 | 400.8297 | 351.2556 | 256.2138 | 299.8494 | 264.5077 | 267.0393 | 213.062 | 176.377 | 122.802
BLD7PRE |  |  | Interior Lighting (elec) | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635
BLD7PRE |  |  | Exterior Lighting (elec) | 70.1181 | 70.0918 | 70.0787 | 70.0682 | 70.0156 | 69.9998 | 70.0366 | 69.9946 | 70.0208 | 69.8815 | 70.0051 | 69.963 | 69.9578 | 69.942 | 69.9026 | 69.4741
BLD7PRE |  |  | Interior Equipment (elec) | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746
BLD7PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans (elec) | 271.6528 | 272.8621 | 287.0234 | 279.208 | 262.31 | 289.9177 | 252.4914 | 266.5293 | 299.4919 | 260.5855 | 250.8563 | 276.7685 | 251.4005 | 265.0124 | 240.9063 | 230.6513
BLD7PRE |  |  | Pumps (elec) | 5.715 | 5.7282 | 5.4311 | 5.807 | 5.347 | 5.2839 | 5.3365 | 5.9358 | 5.2182 | 5.5599 | 6.1199 | 5.4101 | 6.367 | 5.9805 | 6.2907 | 7.1398
BLD7PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification (elec) | 1.4537 | 21.5063 | 85.0155 | 62.024 | 21.7534 | 184.479 | 11.9059 | 98.0334 | 188.6246 | 40.1524 | 111.4429 | 186.0037 | 140.0496 | 180.8145 | 168.856 | 228.4589
BLD7PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 1744.1437 | 1702.0697 | 1774.8954 | 1660.4636 | 1481.1948 | 1790.5184 | 1373.2824 | 1635.8369 | 1671.8542 | 1436.2817 | 1530.2694 | 1564.315 | 1540.8214 | 1522.2804 | 1489.7411 | 1563.9523
BLD7PRE |  |  | Gas (MJ/m2)
BLD7PRE |  |  | Heating (gas) | 675.1744 | 816.5751 | 861.5855 | 951.5012 | 944.3377 | 854.89 | 989.8949 | 996.1462 | 874.4483 | 1049.3952 | 980.2577 | 861.5882 | 1034.574 | 953.2414 | 1042.697 | 1282.9304
BLD7PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
BLD7PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems (gas) | 7.3896 | 8.8118 | 7.9863 | 10.1866 | 9.9211 | 8.9695 | 11.0988 | 11.2644 | 11.0568 | 11.827 | 12.2187 | 12.1687 | 13.031 | 13.1887 | 14.3927 | 16.0278
BLD7PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 732.0827 | 874.9057 | 919.0906 | 1011.2092 | 1003.7802 | 913.3809 | 1050.5125 | 1056.932 | 935.0238 | 1110.7437 | 1041.9952 | 923.2757 | 1097.1265 | 1015.949 | 1106.6086 | 1348.4796
BLD7PRE |  |  | Purchased Cooling (MJ/m2)
BLD7PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Purchased Heating (MJ/m2)
BLD7PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Total Building (MJ/m2) | 2476.2264 | 2576.9753 | 2693.9887 | 2671.6728 | 2484.9751 | 2703.8993 | 2423.7949 | 2692.7663 | 2606.878 | 2547.0254 | 2572.2672 | 2487.5907 | 2637.9478 | 2538.2294 | 2596.3496 | 2912.4345
BLD7PRE |  | Peak Energy Demand
BLD7PRE |  |  | Electricity Peak Demand (kW)
BLD7PRE |  |  | Jan | 341.2837 | 338.1764 | 346.7441 | 334.6738 | 337.5876 | 333.2076 | 297.836 | 357.58 | 345.5156 | 319.8612 | 342.407 | 353.2022 | 362.8237 | 361.0662 | 356.4717 | 384.1203
BLD7PRE |  |  | Feb | 341.1647 | 335.9403 | 366.0071 | 346.7781 | 315.6549 | 334.3545 | 288.0944 | 339.1506 | 344.6616 | 304.293 | 304.9452 | 321.2601 | 336.4214 | 354.0571 | 345.5941 | 374.3227
BLD7PRE |  |  | Mar | 344.2656 | 324.3942 | 399.9372 | 344.0429 | 331.715 | 343.9857 | 275.349 | 327.7504 | 355.6471 | 302.5532 | 298.1243 | 349.696 | 323.9248 | 315.286 | 315.8796 | 355.782
BLD7PRE |  |  | Apr | 349.9591 | 340.5902 | 393.2889 | 332.7575 | 365.105 | 359.9796 | 297.2486 | 309.9622 | 388.9409 | 282.9587 | 286.5467 | 326.6706 | 289.7175 | 309.8001 | 302.7473 | 328.2236
BLD7PRE |  |  | May | 370.1841 | 375.0484 | 421.4825 | 346.8568 | 301.9706 | 424.9799 | 292.6826 | 329.1711 | 386.725 | 294.6748 | 324.4814 | 350.7617 | 319.3273 | 319.7827 | 294.9933 | 302.6031
BLD7PRE |  |  | Jun | 378.5947 | 379.5134 | 501.8471 | 366.007 | 304.5512 | 482.495 | 296.0564 | 372.0616 | 421.8123 | 302.722 | 354.4961 | 376.3503 | 346.9704 | 348.4739 | 308.7626 | 308.444
BLD7PRE |  |  | Jul | 368.1874 | 383.2189 | 439.6243 | 388.0359 | 309.5982 | 457.3235 | 310.3714 | 379.6931 | 426.0532 | 317.7689 | 358.6553 | 372.2931 | 342.4232 | 352.7567 | 322.9446 | 296.713
BLD7PRE |  |  | Aug | 375.4312 | 388.4587 | 440.6621 | 371.5463 | 322.2976 | 424.1082 | 304.8888 | 381.0061 | 370.4119 | 309.0631 | 349.1539 | 370.6694 | 342.9949 | 335.4691 | 315.4236 | 287.7847
BLD7PRE |  |  | Sep | 369.6522 | 373.3382 | 408.1464 | 353.939 | 330.0312 | 425.2847 | 336.836 | 355.0258 | 373.8923 | 312.015 | 330.0375 | 377.4139 | 323.6546 | 317.791 | 298.1295 | 287.8932
BLD7PRE |  |  | Oct | 363.2726 | 355.3349 | 390.0783 | 346.9539 | 345.9157 | 379.8381 | 302.3991 | 328.3486 | 365.9962 | 283.5591 | 310.9007 | 358.3559 | 294.3651 | 308.1546 | 296.7608 | 336.167
BLD7PRE |  |  | Nov | 348.1232 | 338.9538 | 373.8217 | 321.3521 | 315.2254 | 328.8888 | 286.4368 | 313.5545 | 326.6394 | 318.3641 | 310.4535 | 329.4281 | 324.5482 | 308.3873 | 326.8534 | 350.959
BLD7PRE |  |  | Dec | 338.6306 | 329.6335 | 354.6997 | 350.1256 | 338.3257 | 340.4383 | 297.5975 | 335.7024 | 339.3018 | 325.5272 | 324.1053 | 345.6456 | 334.8043 | 363.2271 | 337.4644 | 370.7125
BLD7PRE |  |  | Time of Peak Electrical Demand
BLD7PRE |  |  | Jan | 06-JAN-13:09 | 11-JAN-07:10 | 26-JAN-15:00 | 02-JAN-07:10 | 26-JAN-13:00 | 30-JAN-16:00 | 17-JAN-07:10 | 17-JAN-07:10 | 04-JAN-07:10 | 03-JAN-17:00 | 27-JAN-07:10 | 06-JAN-07:10 | 06-JAN-07:10 | 06-JAN-08:09 | 09-JAN-07:10 | 12-JAN-09:09
BLD7PRE |  |  | Feb | 22-FEB-13:00 | 23-FEB-14:50 | 28-FEB-17:19 | 14-FEB-07:10 | 10-FEB-10:00 | 07-FEB-17:10 | 15-FEB-17:49 | 06-FEB-07:10 | 14-FEB-14:00 | 15-FEB-07:10 | 09-FEB-07:10 | 06-FEB-07:10 | 07-FEB-07:10 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
BLD7PRE |  |  | Mar | 13-MAR-15:50 | 24-MAR-13:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-12:09 | 21-MAR-15:20 | 13-MAR-06:10 | 20-MAR-06:10 | 02-MAR-14:00 | 20-MAR-06:10 | 20-MAR-08:09 | 30-MAR-13:00 | 13-MAR-06:10 | 03-MAR-07:10 | 27-MAR-06:10 | 14-MAR-07:10
BLD7PRE |  |  | Apr | 03-APR-14:09 | 21-APR-14:00 | 26-APR-16:19 | 14-APR-15:00 | 11-APR-16:00 | 21-APR-14:00 | 13-APR-15:00 | 04-APR-15:00 | 21-APR-16:00 | 12-APR-08:00 | 28-APR-16:00 | 26-APR-13:00 | 10-APR-08:09 | 06-APR-16:00 | 03-APR-08:09 | 03-APR-06:10
BLD7PRE |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:19 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:20 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-13:00 | 04-MAY-14:00 | 04-MAY-16:00 | 18-MAY-12:00 | 31-MAY-12:09 | 04-MAY-16:00 | 31-MAY-16:00 | 24-MAY-14:00
BLD7PRE |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-12:09 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 15-JUN-16:19
BLD7PRE |  |  | Jul | 13-JUL-14:00 | 31-JUL-14:30 | 19-JUL-16:00 | 03-JUL-15:39 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-13:00 | 13-JUL-16:10 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
BLD7PRE |  |  | Aug | 21-AUG-14:39 | 31-AUG-13:00 | 01-AUG-16:30 | 17-AUG-13:00 | 08-AUG-12:00 | 18-AUG-14:00 | 15-AUG-12:09 | 17-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 15-AUG-16:00
BLD7PRE |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-12:50 | 20-SEP-14:50 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:49 | 01-SEP-15:09 | 27-SEP-15:00 | 06-SEP-12:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 25-SEP-06:10
BLD7PRE |  |  | Oct | 06-OCT-14:20 | 06-OCT-15:00 | 24-OCT-13:00 | 12-OCT-15:00 | 30-OCT-12:00 | 03-OCT-15:00 | 30-OCT-13:20 | 20-OCT-14:30 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-16:49 | 05-OCT-14:00 | 30-OCT-06:10 | 19-OCT-16:00 | 30-OCT-06:10 | 30-OCT-08:09
BLD7PRE |  |  | Nov | 07-NOV-14:00 | 27-NOV-17:19 | 13-NOV-13:00 | 30-NOV-07:10 | 08-NOV-11:00 | 10-NOV-16:40 | 16-NOV-16:00 | 28-NOV-17:00 | 13-NOV-17:00 | 28-NOV-07:10 | 02-NOV-16:49 | 10-NOV-13:00 | 27-NOV-07:10 | 30-NOV-07:10 | 24-NOV-07:10 | 02-NOV-08:09
BLD7PRE |  |  | Dec | 15-DEC-17:30 | 19-DEC-17:30 | 06-DEC-17:19 | 18-DEC-07:10 | 18-DEC-11:50 | 05-DEC-16:30 | 26-DEC-07:10 | 21-DEC-07:10 | 18-DEC-07:10 | 11-DEC-07:10 | 26-DEC-07:10 | 11-DEC-07:10 | 20-DEC-07:10 | 11-DEC-07:10 | 21-DEC-07:10 | 29-DEC-09:09
BLD7PRE |  | Source Energy
BLD7PRE |  |  | Total Source Energy (GJ) | 25048.48 | 27150.42 | 25173.59 | 25448.98 | 21608.4 | 28157.65 | 20532.02 | 26642.98 | 24985.72 | 14131.65 | 24970.28 | 23579.6 | 24702.74 | 24348.95 | 24074.27 | 26852.44
BLD7PRE |  |  | Total Source Energy (MJ/m2) | 6584.76 | 7137.32 | 6617.65 | 6690.05 | 5680.43 | 7402.1 | 5397.47 | 7003.92 | 6568.26 | 3714.94 | 6564.2 | 6198.62 | 6493.87 | 6400.87 | 6328.66 | 7058.99
BLD7PRE |  | Water Consumption (m3)
BLD7PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Humidification | 2.06 | 30.43 | 120.3 | 87.77 | 30.78 | 261.05 | 16.85 | 138.72 | 266.92 | 56.82 | 157.7 | 263.21 | 198.18 | 255.87 | 238.95 | 323.29
BLD7PRE |  |  | Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
BLD7PRE |  |  | Total Building | 242.53 | 270.91 | 360.78 | 328.25 | 271.26 | 501.53 | 257.33 | 379.2 | 507.4 | 297.3 | 398.18 | 503.69 | 438.66 | 496.35 | 479.43 | 563.77
BLD7PRE |  | Emissions
BLD7PRE |  |  | Carbon Equivalent (kg) | 555655.9079 | 659933.3949 | 629207.5585 | 609834.842 | 251766.5695 | 700774.4652 | 241646.2196 | 538957.3656 | 785791.0149 | 186731.7076 | 933574.4471 | 738566.3047 | 632559.9943 | 657514.236 | 614734.6184 | 557516.6877
BLD7PRE |  |  | CO2 (kg) | 1315460 | 1678760 | 1513590 | 1427060 | 687278.6512 | 1692420 | 660962.2311 | 1255510 | 1866830 | 482718.9688 | 2195600 | 1756340 | 1502240 | 1568550 | 1461520 | 1432130
BLD7PRE |  |  | NOX (kg) | 2195.7902 | 2136.0871 | 2415.7212 | 2550.6048 | 598.5194 | 2642.9217 | 576.4809 | 2281.6354 | 3118.5269 | 621.7571 | 3809.4143 | 2926.6416 | 2541.927 | 2609.7116 | 2465.9066 | 1701.9934
BLD7PRE |  |  | SO2 (kg) | 7889.4482 | 8579.8568 | 7542.6122 | 6159.5425 | 4555.3759 | 10408.3676 | 4223.6139 | 6310.9334 | 7715.3306 | 1174.174 | 10898.2816 | 7219.1067 | 3843.7893 | 4296.0505 | 3716.4048 | 8413.6762
BLD7PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD7PRE |  |  | Hg (kg) | 0.0362 | 0.0245 | 0.0208 | 0.0229 | 0.0025 | 0.0199 | 0.0023 | 0.0259 | 0.0304 | 0.005 | 0.0333 | 0.0285 | 0.0285 | 0.0302 | 0.0275 | 0.029
BLD7PRE |  |  | Water for Electricity (m3) | 976.3347 | 2926.41 | 55710 | 10954.8 | 27480.2 | 51904.7 | 25478.2 | 392.4432 | 8021.76 | 15505.8 | 2508.66 | 7505.78 | 2525.96 | 101892 | 2442.22 | 1688.41
BDL7PST |  | Program
BDL7PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BDL7PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BDL7PST |  |  | Weighting Factor
BDL7PST |  | Fabric
BDL7PST |  |  | Exterior walls
BDL7PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BDL7PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BDL7PST |  |  | Roof
BDL7PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BDL7PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BDL7PST |  |  | Window
BDL7PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BDL7PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BDL7PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BDL7PST |  |  | Skylights/TDD
BDL7PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BDL7PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BDL7PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BDL7PST |  |  | Foundation
BDL7PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BDL7PST |  |  | Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
BDL7PST |  |  | R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
BDL7PST |  | HVAC
BDL7PST |  |  | HVAC Sizing
BDL7PST | HVAC |  | Air Conditioning (kW) | 616.0277 | 574.513 | 581.4893 | 545.2917 | 469.4937 | 512.6577 | 397.2252 | 529.7863 | 447.0554 | 414.9117 | 528.8816 | 430.489 | 508.3226 | 413.0393 | 448.0943 | 391.9223
BDL7PST |  |  | AHU-1_COOLC DXCOIL | 286.8035 | 269.2847 | 266.6469 | 255.4428 | 219.1736 | 235.9666 | 186.385 | 251.0221 | 218.8229 | 195.2891 | 251.2542 | 214.6713 | 244.1834 | 205.5078 | 215.4211 | 189.5021
BDL7PST |  |  | AHU-2_COOLC DXCOIL | 329.2242 | 305.2283 | 314.8425 | 289.849 | 250.3202 | 276.6911 | 210.8402 | 278.7642 | 228.2325 | 219.6227 | 277.6274 | 215.8177 | 264.1392 | 207.5315 | 232.6732 | 202.4202
BDL7PST |  |  | Heating (kW)
BDL7PST | HEAT |  | HEATSYS1 BOILER | 135.6875 | 131.4663 | 127.2951 | 132.1069 | 126.3248 | 121.191 | 121.3352 | 135.6571 | 120.4736 | 126.737 | 145.764 | 128.8369 | 151.4411 | 142.1619 | 151.5431 | 174.2775
BDL7PST |  |  | HVAC Efficiency
BDL7PST | COP |  | Air Conditioning (COP) | 2.73 | 2.73 | 2.73 | 2.73 | 2.7627 | 2.73 | 2.8 | 2.73 | 2.7643 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.7637 | 2.8
BDL7PST |  |  | AHU-1_COOLC DXCOIL | 2.73 | 2.73 | 2.73 | 2.73 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.8 | 2.8
BDL7PST |  |  | AHU-2_COOLC DXCOIL | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.8 | 2.73 | 2.73 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8
BDL7PST |  |  | Heating Efficiency (%)
BDL7PST | EffHeat |  | HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BDL7PST |  |  | HVAC Control - Economizer
BDL7PST |  |  | AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BDL7PST |  |  | AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BDL7PST | Fan |  | Fan Max Flow Rate (m3/s ) | 28.04 | 25.24 | 27.42 | 25.49 | 25.92 | 26.68 | 23.67 | 23.91 | 27.01 | 24.05 | 24.05 | 26.01 | 23.59 | 24.95 | 23.2 | 23.68
BDL7PST |  |  | AHU-1_FAN | 13.29 | 12.15 | 12.84 | 12.22 | 12.38 | 12.6 | 11.26 | 11.65 | 13.22 | 11.61 | 11.77 | 12.97 | 11.73 | 12.41 | 11.56 | 11.45
BDL7PST |  |  | AHU-2_FAN | 14.75 | 13.09 | 14.58 | 13.27 | 13.54 | 14.08 | 12.41 | 12.26 | 13.79 | 12.44 | 12.28 | 13.04 | 11.86 | 12.54 | 11.64 | 12.23
BDL7PST |  | Utility Costs
BDL7PST |  |  | Electric Utility Rates
BDL7PST |  |  | Average Annual Rate ($/kWh) | 0.080165 | 0.10702 | 0.078327 | 0.098916 | 0.12324 | 0.09154 | 0.14444 | 0.069075 | 0.037042 | 0.071677 | 0.096473 | 0.037047 | 0.054354 | 0.071664 | 0.054275 | 0.091169
BDL7PST |  |  | Total Cost ($/m2) | 41 | 49.76 | 38.29 | 43.67 | 51.08 | 43.92 | 53.18 | 29.54 | 16.37 | 27.1 | 40.2 | 15.78 | 22.62 | 29.45 | 21.85 | 38.38
BDL7PST |  |  | Gas Utility Rates
BDL7PST |  |  | Average Annual Rate ($/MJ) | 0.011406 | 0.0081604 | 0.0085862 | 0.010809 | 0.0083903 | 0.0081365 | 0.0083875 | 0.01011 | 0.0072235 | 0.0082712 | 0.0089819 | 0.0072313 | 0.0079826 | 0.0088559 | 0.0079909 | 0.0041922
BDL7PST |  |  | Total Cost ($/m2) | 8.98 | 7 | 7.94 | 10.32 | 8.59 | 7.25 | 8.25 | 9.87 | 6.41 | 8.53 | 9.29 | 6.65 | 8.63 | 8.84 | 8.88 | 5.78
BDL7PST |  |  | Total Utility Costs
BDL7PST |  |  | Cost Intensity ($/m2) | 49.98 | 56.77 | 46.23 | 53.98 | 59.67 | 51.17 | 61.43 | 39.41 | 22.78 | 35.64 | 49.49 | 22.42 | 31.25 | 38.29 | 30.73 | 44.16
BDL7PST |  | Energy - End Uses
BDL7PST |  |  | Electricity (kWh)
BDL7PST |  |  | Heating | 13044.4444 | 33286.1111 | 33233.3333 | 51858.3333 | 35038.8889 | 38630.5556 | 45369.4444 | 64322.2222 | 44352.7778 | 75094.4444 | 81652.7778 | 52363.8889 | 89177.7778 | 74480.5556 | 101427.7778 | 162750
BDL7PST |  |  | Cooling | 834647.2222 | 648575 | 655994.4444 | 502066.6667 | 449238.8889 | 529458.3333 | 299855.5556 | 417052.7778 | 365055.5556 | 273858.3333 | 336661.1111 | 296691.6667 | 298544.4444 | 238769.4444 | 203872.2222 | 146863.8889
BDL7PST |  |  | Interior Lighting | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667
BDL7PST |  |  | Exterior Lighting | 74091.6667 | 74063.8889 | 74050 | 74038.8889 | 73983.3333 | 73966.6667 | 74005.5556 | 73961.1111 | 73988.8889 | 73841.6667 | 73972.2222 | 73927.7778 | 73922.2222 | 73905.5556 | 73863.8889 | 73411.1111
BDL7PST |  |  | Interior Equipment | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778
BDL7PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans | 295391.6667 | 265569.4444 | 285658.3333 | 265500 | 269791.6667 | 278952.7778 | 243766.6667 | 251680.5556 | 288844.4444 | 250872.2222 | 253883.3333 | 281280.5556 | 253455.5556 | 267661.1111 | 250058.3333 | 246744.4444
BDL7PST |  |  | Pumps | 5941.6667 | 5750 | 5569.4444 | 5777.7778 | 5530.5556 | 5294.4444 | 5311.1111 | 5905.5556 | 5263.8889 | 5544.4444 | 6341.6667 | 5625 | 6594.4444 | 6183.3333 | 6602.7778 | 7516.6667
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 1600 | 20852.7778 | 84441.6667 | 59205.5556 | 22300 | 177911.1111 | 11355.5556 | 92838.8889 | 182325 | 38494.4444 | 111880.5556 | 189183.3333 | 140775 | 181691.6667 | 175102.7778 | 243411.1111
BDL7PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 1945511.1111 | 1768894.4444 | 1859738.8889 | 1679247.2222 | 1576677.7778 | 1825008.3333 | 1400461.1111 | 1626555.5556 | 1680625 | 1438500 | 1585183.3333 | 1619866.6667 | 1583266.6667 | 1563486.1111 | 1531719.4444 | 1601494.4444
BDL7PST |  |  | Gas (MJ)
BDL7PST |  |  | Heating | 2778310 | 3041030 | 3296200 | 3403580 | 3665620 | 3167940 | 3508990 | 3481260 | 3146490 | 3689280 | 3699140 | 3261640 | 3872850 | 3557370 | 3982480 | 4995550
BDL7PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
BDL7PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems | 28810 | 34370 | 31140 | 39730 | 38690 | 34980 | 43280 | 43930 | 43120 | 46130 | 47650 | 47460 | 50860 | 51440 | 56140 | 62520
BDL7PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 2995490 | 3263770 | 3515710 | 3631690 | 3892690 | 3391300 | 3740650 | 3713570 | 3377990 | 3923790 | 3935170 | 3497470 | 4112090 | 3797180 | 4226990 | 5246450
BDL7PST |  |  | Purchased Cooling (MJ)
BDL7PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Purchased Heating (MJ)
BDL7PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total Building (MJ) | 9999330 | 9631790 | 10210770 | 9676970 | 9568730 | 9961330 | 8782310 | 9569160 | 9428240 | 9102380 | 9641820 | 9329000 | 9811840 | 9425730 | 9741180 | 11011830
BDL7PST |  | Energy - End Use Intensities
BDL7PST |  |  | Electricity (MJ/m2)
BDL7PST |  |  | Heating (elec) | 12.3449 | 31.501 | 31.451 | 49.0772 | 33.1597 | 36.5588 | 42.9363 | 60.8726 | 41.9741 | 71.0671 | 77.2737 | 49.5556 | 84.3952 | 70.4861 | 95.9882 | 154.0217
BDL7PST |  |  | Cooling (elec) | 789.8849 | 613.7918 | 620.8133 | 475.1407 | 425.1461 | 501.0634 | 283.7742 | 394.6861 | 345.4775 | 259.1712 | 318.6059 | 280.78 | 282.5334 | 225.9642 | 192.9385 | 138.9875
BDL7PST |  |  | Interior Lighting (elec) | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635
BDL7PST |  |  | Exterior Lighting (elec) | 70.1181 | 70.0918 | 70.0787 | 70.0682 | 70.0156 | 69.9998 | 70.0366 | 69.9946 | 70.0208 | 69.8815 | 70.0051 | 69.963 | 69.9578 | 69.942 | 69.9026 | 69.4741
BDL7PST |  |  | Interior Equipment (elec) | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746
BDL7PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans (elec) | 279.5497 | 251.3269 | 270.3384 | 251.2612 | 255.3227 | 263.9925 | 230.6934 | 238.1829 | 273.3536 | 237.4179 | 240.2675 | 266.1954 | 239.8627 | 253.3064 | 236.6476 | 233.5115
BDL7PST |  |  | Pumps (elec) | 5.623 | 5.4416 | 5.2708 | 5.4679 | 5.234 | 5.0105 | 5.0263 | 5.5888 | 4.9816 | 5.2471 | 6.0016 | 5.3233 | 6.2408 | 5.8517 | 6.2487 | 7.1135
BDL7PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification (elec) | 1.5142 | 19.7344 | 79.913 | 56.0303 | 21.104 | 168.3697 | 10.7466 | 87.8599 | 172.5469 | 36.43 | 105.8804 | 179.0374 | 133.2252 | 171.9475 | 165.712 | 230.3569
BDL7PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 1841.1729 | 1674.0282 | 1760.0006 | 1589.1888 | 1492.1202 | 1727.1327 | 1325.354 | 1539.323 | 1590.4927 | 1361.3529 | 1500.1696 | 1532.9928 | 1498.3557 | 1479.636 | 1449.573 | 1515.6059
BDL7PST |  |  | Gas (MJ/m2)
BDL7PST |  |  | Heating (gas) | 730.3635 | 799.4274 | 866.5067 | 894.7348 | 963.62 | 832.7896 | 922.445 | 915.1553 | 827.1508 | 969.8397 | 972.4317 | 857.4215 | 1018.0967 | 935.1632 | 1046.9163 | 1313.2326
BDL7PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
BDL7PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems (gas) | 7.5736 | 9.0352 | 8.1861 | 10.4442 | 10.1708 | 9.1956 | 11.3775 | 11.5483 | 11.3354 | 12.1267 | 12.5263 | 12.4763 | 13.3701 | 13.5226 | 14.7581 | 16.4353
BDL7PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 787.4559 | 857.9814 | 924.2116 | 954.7004 | 1023.3122 | 891.5066 | 983.3439 | 976.2251 | 888.0077 | 1031.4878 | 1034.4794 | 919.4166 | 1080.9882 | 998.2045 | 1111.1932 | 1379.1893
BDL7PST |  |  | Purchased Cooling (MJ/m2)
BDL7PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Purchased Heating (MJ/m2)
BDL7PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Total Building (MJ/m2) | 2628.6287 | 2532.0096 | 2684.2122 | 2543.8866 | 2515.4324 | 2618.6393 | 2308.6979 | 2515.5454 | 2478.5003 | 2392.8381 | 2534.6463 | 2452.4121 | 2579.3413 | 2477.8405 | 2560.7661 | 2894.7952
BDL7PST |  | Peak Energy Demand
BDL7PST |  |  | Electricity Peak Demand (kW)
BDL7PST |  |  | Jan | 351.7617 | 335.42 | 342.1046 | 306.2954 | 341.6143 | 324.055 | 278.9807 | 319.6956 | 315.6498 | 299.5163 | 348.3721 | 330.6245 | 343.4463 | 351.9208 | 347.2728 | 385.9663
BDL7PST |  |  | Feb | 357.4768 | 330.2036 | 361.6186 | 312.582 | 317.9031 | 327.0362 | 287.2511 | 305.9119 | 332.18 | 279.9633 | 292.2291 | 305.5707 | 313.7784 | 333.7046 | 323.8527 | 352.4819
BDL7PST |  |  | Mar | 361.0189 | 325.5666 | 395.671 | 332.706 | 334.8761 | 331.8934 | 266.645 | 306.9737 | 343.5946 | 278.3322 | 287.109 | 348.7159 | 304.2495 | 310.5792 | 296.13 | 332.4717
BDL7PST |  |  | Apr | 367.7395 | 340.6957 | 388.9422 | 328.4834 | 369.4794 | 350.4356 | 291.4577 | 304.2753 | 379.1471 | 275.5866 | 288.6751 | 328.2817 | 283.1911 | 311.2965 | 285.3638 | 310.1424
BDL7PST |  |  | May | 389.8239 | 372.7968 | 416.9051 | 343.8535 | 305.8807 | 413.8993 | 289.3258 | 326.5397 | 373.8388 | 290.5297 | 327.68 | 352.1484 | 323.887 | 321.4923 | 300.2032 | 313.0997
BDL7PST |  |  | Jun | 400.9024 | 376.9163 | 497.5041 | 358.578 | 308.9648 | 467.2832 | 292.4751 | 368.3755 | 408.4364 | 298.3723 | 359.8627 | 374.2173 | 350.6225 | 353.1295 | 316.4893 | 317.9088
BDL7PST |  |  | Jul | 387.4647 | 379.1577 | 443.8997 | 380.1265 | 314.2392 | 441.8366 | 305.2487 | 372.9904 | 410.1113 | 311.2731 | 363.1668 | 369.1095 | 348.0783 | 354.0181 | 328.7173 | 306.1844
BDL7PST |  |  | Aug | 397.4916 | 385.0278 | 442.2988 | 363.4671 | 327.5939 | 407.8575 | 299.7347 | 371.9186 | 355.1227 | 302.7964 | 354.9109 | 368.1173 | 347.8164 | 336.8123 | 322.589 | 296.6809
BDL7PST |  |  | Sep | 389.7029 | 373.4634 | 405.6355 | 345.339 | 335.2429 | 407.6558 | 329.5637 | 345.9737 | 364.9469 | 307.8686 | 335.9421 | 375.1284 | 327.9538 | 320.7134 | 305.439 | 276.5238
BDL7PST |  |  | Oct | 382.8024 | 355.2212 | 385.2831 | 341.3645 | 348.9459 | 370.3047 | 295.9194 | 324.6748 | 353.0935 | 278.5899 | 316.2812 | 358.2367 | 287.501 | 309.5484 | 283.8634 | 321.0342
BDL7PST |  |  | Nov | 365.2649 | 341.2682 | 369.4778 | 300.7525 | 318.454 | 324.6616 | 278.6927 | 308.8059 | 320.4295 | 294.5807 | 315.7257 | 330.665 | 305.359 | 294.12 | 307.9501 | 333.5688
BDL7PST |  |  | Dec | 352.5185 | 330.2368 | 351.1293 | 320.8906 | 341.0617 | 334.1632 | 283.3969 | 299.0145 | 310.5269 | 298.8879 | 310.1917 | 325.2075 | 311.6556 | 342.7808 | 314.7393 | 349.55
BDL7PST |  |  | Time of Peak Electrical Demand
BDL7PST |  |  | Jan | 06-JAN-13:00 | 03-JAN-13:00 | 26-JAN-15:00 | 30-JAN-07:10 | 26-JAN-13:00 | 30-JAN-16:00 | 17-JAN-07:10 | 17-JAN-07:10 | 09-JAN-07:10 | 03-JAN-17:00 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-08:09 | 09-JAN-07:10 | 17-JAN-09:09
BDL7PST |  |  | Feb | 23-FEB-11:00 | 23-FEB-14:39 | 28-FEB-17:19 | 14-FEB-07:10 | 10-FEB-10:00 | 07-FEB-17:10 | 15-FEB-17:49 | 06-FEB-07:10 | 14-FEB-14:00 | 21-FEB-17:40 | 23-FEB-17:30 | 08-FEB-17:30 | 06-FEB-07:10 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
BDL7PST |  |  | Mar | 13-MAR-15:50 | 24-MAR-13:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-12:09 | 17-MAR-15:00 | 13-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 20-MAR-06:10 | 08-MAR-17:00 | 30-MAR-13:00 | 13-MAR-06:10 | 30-MAR-16:19 | 06-MAR-17:00 | 14-MAR-07:10
BDL7PST |  |  | Apr | 03-APR-14:09 | 21-APR-14:00 | 26-APR-16:19 | 14-APR-15:00 | 11-APR-16:00 | 21-APR-16:19 | 13-APR-16:10 | 04-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 28-APR-16:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-16:00 | 03-APR-08:09 | 03-APR-06:10
BDL7PST |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:19 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-13:00 | 05-MAY-15:00 | 04-MAY-16:00 | 18-MAY-12:00 | 31-MAY-12:09 | 04-MAY-16:00 | 31-MAY-16:00 | 24-MAY-14:00
BDL7PST |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 28-JUN-12:09 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 15-JUN-16:19
BDL7PST |  |  | Jul | 13-JUL-14:00 | 12-JUL-14:30 | 19-JUL-16:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-16:19 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-16:19 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 13-JUL-15:39 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
BDL7PST |  |  | Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-16:00 | 17-AUG-13:00 | 08-AUG-12:00 | 18-AUG-14:00 | 15-AUG-12:09 | 17-AUG-15:09 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 15-AUG-16:00
BDL7PST |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-12:00 | 21-SEP-14:39 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:00 | 01-SEP-15:39 | 27-SEP-15:00 | 06-SEP-12:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 25-SEP-06:10
BDL7PST |  |  | Oct | 06-OCT-14:20 | 06-OCT-15:00 | 24-OCT-13:00 | 12-OCT-15:00 | 30-OCT-12:00 | 03-OCT-15:00 | 30-OCT-13:20 | 20-OCT-15:39 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-16:49 | 05-OCT-14:00 | 06-OCT-14:00 | 19-OCT-16:00 | 30-OCT-06:10 | 30-OCT-08:09
BDL7PST |  |  | Nov | 07-NOV-14:00 | 27-NOV-17:19 | 13-NOV-13:00 | 16-NOV-17:40 | 08-NOV-11:00 | 10-NOV-16:40 | 16-NOV-16:00 | 03-NOV-13:00 | 08-NOV-17:19 | 20-NOV-07:10 | 02-NOV-16:49 | 10-NOV-13:00 | 27-NOV-07:10 | 27-NOV-07:10 | 24-NOV-07:10 | 06-NOV-08:09
BDL7PST |  |  | Dec | 15-DEC-17:30 | 19-DEC-17:30 | 06-DEC-17:19 | 18-DEC-07:10 | 18-DEC-11:50 | 05-DEC-16:30 | 29-DEC-16:00 | 11-DEC-07:10 | 18-DEC-07:10 | 11-DEC-07:10 | 26-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 21-DEC-07:10 | 29-DEC-09:09
BDL7PST |  | Source Energy
BDL7PST |  |  | Total Source Energy (GJ) | 26502.81 | 26692.68 | 25015.63 | 24302.14 | 21818.15 | 27204.28 | 19688.72 | 24994.83 | 23763.51 | 13305.89 | 24533.01 | 23168.23 | 24080.47 | 23711.35 | 23568.16 | 26323.05
BDL7PST |  |  | Total Source Energy (MJ/m2) | 6967.08 | 7016.99 | 6576.13 | 6388.56 | 5735.57 | 7151.48 | 5175.78 | 6570.66 | 6246.97 | 3497.86 | 6449.25 | 6090.48 | 6330.29 | 6233.26 | 6195.61 | 6919.82
BDL7PST |  | Water Consumption (m3)
BDL7PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Humidification | 2.14 | 27.93 | 113.08 | 79.29 | 29.86 | 238.26 | 15.21 | 124.33 | 244.17 | 51.55 | 149.83 | 253.35 | 188.52 | 243.32 | 234.5 | 325.98
BDL7PST |  |  | Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
BDL7PST |  |  | Total Building | 242.62 | 268.4 | 353.56 | 319.77 | 270.34 | 478.74 | 255.69 | 364.81 | 484.65 | 292.03 | 390.31 | 493.83 | 429 | 483.8 | 474.98 | 566.46
BDL7PST |  | Emissions
BDL7PST |  |  | Carbon Equivalent (kg) | 587572.6583 | 648888.4922 | 624807.3466 | 582758.5013 | 254455.3546 | 676683.7261 | 231120.0328 | 505900.3267 | 747446.748 | 175528.3064 | 916100.9166 | 724781.5482 | 616092.9568 | 639829.6339 | 600521.255 | 545247.7917
BDL7PST |  |  | CO2 (kg) | 1391540 | 1650610 | 1503430 | 1363210 | 694751.1708 | 1634580 | 631848.3841 | 1177800 | 1775680 | 453312.6277 | 2154990 | 1724070 | 1463630 | 1526730 | 1428940 | 1402200
BDL7PST |  |  | NOX (kg) | 2320.581 | 2100.4425 | 2397.7566 | 2438.7608 | 605.1158 | 2551.2411 | 550.8725 | 2143.7178 | 2966.4919 | 585.4863 | 3736.8167 | 2870.6739 | 2474.405 | 2538.5309 | 2405.6142 | 1662.4044
BDL7PST |  |  | SO2 (kg) | 8328.3673 | 8438.4981 | 7479.3242 | 5895.1263 | 4588.9829 | 10039.9089 | 4076.1733 | 5938.5704 | 7339.8645 | 1112.8961 | 10683.9207 | 7074.5744 | 3737.8636 | 4175.7111 | 3616.2386 | 8153.652
BDL7PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7PST |  |  | Hg (kg) | 0.0383 | 0.0241 | 0.0207 | 0.0219 | 0.0025 | 0.0192 | 0.0022 | 0.0243 | 0.0289 | 0.0048 | 0.0326 | 0.0279 | 0.0277 | 0.0293 | 0.0268 | 0.0281
BDL7PST |  |  | Water for Electricity (m3) | 1030.65 | 2878.2 | 55242.4 | 10484.5 | 27682.9 | 50067.2 | 24588.9 | 369.2891 | 7631.39 | 14696.9 | 2459.32 | 7355.49 | 2456.34 | 99037.7 | 2376.37 | 1636.21
BDL7NEW |  | Program
BDL7NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BDL7NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BDL7NEW |  |  | Weighting Factor | 12.0363 | 183.3674 | 43.3615 | 187.8142 |  | 88.8067 | 19.7797 | 264.2744 | 7.5099 | 58.4502 | 342.01 | 70.3698 | 110.6579 | 10.7551 | 12.5902 | 0.66527
BDL7NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BDL7NEW |  |  | Exterior walls
BDL7NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BDL7NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BDL7NEW |  |  | Roof
BDL7NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BDL7NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BDL7NEW |  |  | Window
BDL7NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BDL7NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BDL7NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BDL7NEW |  |  | Skylights/TDD
BDL7NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BDL7NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BDL7NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BDL7NEW |  |  | Foundation
BDL7NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BDL7NEW |  |  | Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
BDL7NEW |  |  | R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
BDL7NEW |  | HVAC
BDL7NEW |  |  | HVAC Sizing
BDL7NEW | HVAC |  | Air Conditioning (kW) | 498.5725 | 504.5554 | 502.518 | 476.8165 | 382.0583 | 443.7767 | 362.9994 | 480.54 | 408.643 | 374.4653 | 472.8985 | 396.384 | 461.1064 | 382.7874 | 411.7201 | 319.6834
BDL7NEW |  |  | AHU-1_COOLC DXCOIL | 239.0574 | 237.8764 | 229.0538 | 225.7241 | 185.7094 | 201.2808 | 171.2715 | 225.3641 | 196.7908 | 175.2028 | 222.4906 | 192.5701 | 218.001 | 184.9672 | 192.6326 | 156.1667
BDL7NEW |  |  | AHU-2_COOLC DXCOIL | 259.5151 | 266.679 | 273.4642 | 251.0924 | 196.3489 | 242.4959 | 191.7279 | 255.1759 | 211.8523 | 199.2625 | 250.4079 | 203.8138 | 243.1055 | 197.8202 | 219.0875 | 163.5167
BDL7NEW |  |  | Heating (kW)
BDL7NEW | HEAT |  | HEATSYS1 BOILER | 124.739 | 125.1364 | 115.3736 | 124.9673 | 115.0652 | 113.5958 | 117.9526 | 130.357 | 114.6396 | 122.5312 | 139.2338 | 122.7386 | 143.0675 | 133.9838 | 143.2942 | 159.0514
BDL7NEW |  |  | HVAC Efficiency
BDL7NEW | COP |  | Air Conditioning (COP) | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.1754 | 3.23 | 3.13 | 3.23 | 3.23 | 3.177 | 3.23 | 3.1773 | 3.23 | 3.23 | 3.23
BDL7NEW |  |  | AHU-1_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BDL7NEW |  |  | AHU-2_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.13 | 3.23 | 3.13 | 3.23 | 3.23 | 3.13 | 3.23 | 3.13 | 3.23 | 3.23 | 3.23
BDL7NEW |  |  | Heating Efficiency (%)
BDL7NEW | EffHeat |  | HEATSYS1 BOILER | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
BDL7NEW |  |  | HVAC Control - Economizer
BDL7NEW |  |  | AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BDL7NEW |  |  | AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BDL7NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 21.9 | 22.25 | 23.48 | 22.25 | 20.62 | 22.98 | 21.61 | 22.05 | 24.69 | 21.62 | 21.77 | 23.94 | 21.83 | 23.12 | 21.67 | 19.31
BDL7NEW |  |  | AHU-1_FAN | 10.67 | 10.73 | 10.83 | 10.74 | 10.24 | 10.67 | 10.35 | 10.57 | 11.89 | 10.37 | 10.47 | 11.63 | 10.54 | 11.17 | 10.42 | 9.43
BDL7NEW |  |  | AHU-2_FAN | 11.23 | 11.52 | 12.65 | 11.51 | 10.38 | 12.31 | 11.26 | 11.48 | 12.8 | 11.25 | 11.3 | 12.31 | 11.29 | 11.95 | 11.25 | 9.88
BDL7NEW |  | Utility Costs
BDL7NEW |  |  | Electric Utility Rates
BDL7NEW |  |  | Average Annual Rate ($/kWh) | 0.080422 | 0.10724 | 0.080411 | 0.099098 | 0.12353 | 0.095539 | 0.14454 | 0.069274 | 0.03706 | 0.071891 | 0.096404 | 0.037065 | 0.054617 | 0.071735 | 0.054479 | 0.091464
BDL7NEW |  |  | Total Cost ($/m2) | 32.82 | 42.03 | 32.37 | 36.88 | 41.72 | 37.65 | 46.42 | 25.67 | 14.16 | 23.46 | 34.35 | 13.69 | 19.71 | 25.78 | 19.21 | 32.33
BDL7NEW |  |  | Gas Utility Rates
BDL7NEW |  |  | Average Annual Rate ($/MJ) | 0.011419 | 0.0081636 | 0.0085953 | 0.010826 | 0.0083853 | 0.0081505 | 0.0083855 | 0.010109 | 0.0072254 | 0.0082707 | 0.0089806 | 0.0072323 | 0.0079817 | 0.008852 | 0.0079898 | 0.0041911
BDL7NEW |  |  | Total Cost ($/m2) | 7.03 | 5.78 | 6.24 | 8.46 | 6.51 | 5.68 | 7.13 | 8.4 | 5.42 | 7.11 | 7.73 | 5.59 | 7.3 | 7.49 | 7.51 | 4.56
BDL7NEW |  |  | Total Utility Costs
BDL7NEW |  |  | Cost Intensity ($/m2) | 39.85 | 47.81 | 38.61 | 45.34 | 48.23 | 43.33 | 53.55 | 34.07 | 19.59 | 30.57 | 42.09 | 19.28 | 27.01 | 33.28 | 26.71 | 36.89
BDL7NEW |  | Energy - End Uses
BDL7NEW |  |  | Electricity (kWh)
BDL7NEW |  |  | Heating | 2750 | 20816.6667 | 17477.7778 | 29069.4444 | 8694.4444 | 18180.5556 | 30847.2222 | 51352.7778 | 32391.6667 | 53158.3333 | 58491.6667 | 39622.2222 | 74955.5556 | 62761.1111 | 84986.1111 | 114708.3333
BDL7NEW |  |  | Cooling | 591175 | 497258.3333 | 487636.1111 | 383083.3333 | 317280.5556 | 385605.5556 | 237102.7778 | 328241.6667 | 284688.8889 | 211827.7778 | 255002.7778 | 231925 | 228186.1111 | 187141.6667 | 158988.8889 | 105688.8889
BDL7NEW |  |  | Interior Lighting | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111 | 156236.1111
BDL7NEW |  |  | Exterior Lighting | 61608.3333 | 61586.1111 | 61575 | 61563.8889 | 61516.6667 | 61502.7778 | 61536.1111 | 61500 | 61522.2222 | 61400 | 61508.3333 | 61472.2222 | 61469.4444 | 61455.5556 | 61419.4444 | 61044.4444
BDL7NEW |  |  | Interior Equipment | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778
BDL7NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans | 234483.3333 | 233108.3333 | 239219.4444 | 231930.5556 | 219658.3333 | 234708.3333 | 221594.4444 | 227780.5556 | 259883.3333 | 222430.5556 | 225180.5556 | 251833.3333 | 227100 | 240466.6667 | 224694.4444 | 212491.6667
BDL7NEW |  |  | Pumps | 5430.5556 | 5436.1111 | 5013.8889 | 5430.5556 | 4977.7778 | 4922.2222 | 5113.8889 | 5644.4444 | 4997.2222 | 5319.4444 | 6027.7778 | 5333.3333 | 6200 | 5805.5556 | 6213.8889 | 6822.2222
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 997.2222 | 16533.3333 | 64552.7778 | 48738.8889 | 16658.3333 | 138005.5556 | 9636.1111 | 79036.1111 | 154227.7778 | 31144.4444 | 93377.7778 | 159169.4444 | 119044.4444 | 153633.3333 | 148680.5556 | 187783.3333
BDL7NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 1552455.5556 | 1490752.7778 | 1531488.8889 | 1415827.7778 | 1284802.7778 | 1498941.6667 | 1221841.6667 | 1409569.4444 | 1453725 | 1241294.4444 | 1355600 | 1405369.4444 | 1372966.6667 | 1367275 | 1340997.2222 | 1344547.2222
BDL7NEW |  |  | Gas (MJ)
BDL7NEW |  |  | Heating | 2125390 | 2470790 | 2541070 | 2745050 | 2724900 | 2428430 | 3003760 | 2928530 | 2624750 | 3037450 | 3040290 | 2703810 | 3240530 | 2981850 | 3331820 | 3892890
BDL7NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
BDL7NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems | 28110 | 33520 | 30380 | 38750 | 37740 | 34120 | 42220 | 42850 | 42060 | 44990 | 46480 | 46290 | 49570 | 50170 | 54750 | 60970
BDL7NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 2341870 | 2692690 | 2759820 | 2972180 | 2951020 | 2650930 | 3234350 | 3159760 | 2855180 | 3270820 | 3275140 | 2938470 | 3478480 | 3220390 | 3574940 | 4142240
BDL7NEW |  |  | Purchased Cooling (MJ)
BDL7NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Purchased Heating (MJ)
BDL7NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total Building (MJ) | 7930720 | 8059400 | 8273180 | 8069160 | 7576310 | 8047120 | 7632980 | 8234210 | 8088590 | 7739470 | 8155300 | 7997800 | 8421160 | 8142590 | 8402530 | 8982610
BDL7NEW |  | Energy - End Use Intensities
BDL7NEW |  |  | Electricity (MJ/m2)
BDL7NEW |  |  | Heating (elec) | 2.6025 | 19.7003 | 16.5404 | 27.5104 | 8.2282 | 17.2055 | 29.1929 | 48.5987 | 30.6545 | 50.3074 | 55.3547 | 37.4973 | 70.9357 | 59.3952 | 80.4283 | 108.5565
BDL7NEW |  |  | Cooling (elec) | 559.4701 | 470.5902 | 461.4841 | 362.5385 | 300.2647 | 364.9254 | 224.3869 | 310.638 | 269.421 | 200.4674 | 241.3269 | 219.4868 | 215.9484 | 177.1052 | 150.4623 | 100.0208
BDL7NEW |  |  | Interior Lighting (elec) | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571 | 147.8571
BDL7NEW |  |  | Exterior Lighting (elec) | 58.3043 | 58.2832 | 58.2727 | 58.2622 | 58.2175 | 58.2044 | 58.2359 | 58.2017 | 58.2228 | 58.1071 | 58.2096 | 58.1755 | 58.1728 | 58.1597 | 58.1255 | 57.7706
BDL7NEW |  |  | Interior Equipment (elec) | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746
BDL7NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans (elec) | 221.9079 | 220.6067 | 226.39 | 219.4921 | 207.878 | 222.1209 | 209.7103 | 215.5646 | 245.9457 | 210.5015 | 213.1041 | 238.3274 | 214.9206 | 227.5704 | 212.644 | 201.0957
BDL7NEW |  |  | Pumps (elec) | 5.1393 | 5.1446 | 4.745 | 5.1393 | 4.7108 | 4.6582 | 4.8396 | 5.3417 | 4.7292 | 5.0342 | 5.7045 | 5.0473 | 5.8675 | 5.4942 | 5.8806 | 6.4563
BDL7NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification (elec) | 0.94374 | 15.6466 | 61.0908 | 46.125 | 15.7649 | 130.6043 | 9.1193 | 74.7974 | 145.9565 | 29.4742 | 88.3699 | 150.6331 | 112.6601 | 145.3939 | 140.7068 | 177.7125
BDL7NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 1469.197 | 1410.8033 | 1449.3548 | 1339.8966 | 1215.8985 | 1418.5531 | 1156.314 | 1333.9739 | 1375.7614 | 1174.7235 | 1282.8988 | 1329.9991 | 1299.3341 | 1293.9477 | 1269.0792 | 1272.4388
BDL7NEW |  |  | Gas (MJ/m2)
BDL7NEW |  |  | Heating (gas) | 558.7236 | 649.5225 | 667.9977 | 721.6201 | 716.323 | 638.3869 | 789.6299 | 769.8534 | 689.9956 | 798.4863 | 799.2329 | 710.7789 | 851.8721 | 783.8702 | 875.8705 | 1023.3648
BDL7NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
BDL7NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems (gas) | 7.3896 | 8.8118 | 7.9863 | 10.1866 | 9.9211 | 8.9695 | 11.0988 | 11.2644 | 11.0568 | 11.827 | 12.2187 | 12.1687 | 13.031 | 13.1887 | 14.3927 | 16.0278
BDL7NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 615.6319 | 707.8557 | 725.5028 | 781.3281 | 775.7656 | 696.8778 | 850.2475 | 830.6392 | 750.5711 | 859.8348 | 860.9704 | 772.4664 | 914.4245 | 846.5777 | 939.782 | 1088.9141
BDL7NEW |  |  | Purchased Cooling (MJ/m2)
BDL7NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Purchased Heating (MJ/m2)
BDL7NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Total Building (MJ/m2) | 2084.8315 | 2118.659 | 2174.8576 | 2121.2247 | 1991.6641 | 2115.4308 | 2006.5615 | 2164.6131 | 2126.3325 | 2034.5556 | 2143.8692 | 2102.4656 | 2213.7586 | 2140.528 | 2208.8612 | 2361.3529
BDL7NEW |  | Peak Energy Demand
BDL7NEW |  |  | Electricity Peak Demand (kW)
BDL7NEW |  |  | Jan | 294.8016 | 288.0118 | 288.056 | 259.886 | 281.4216 | 275.5915 | 243.9994 | 285.2281 | 274.8997 | 262.4887 | 301.3492 | 300.1374 | 314.1468 | 315.3248 | 316.3809 | 327.9224
BDL7NEW |  |  | Feb | 290.7202 | 283.9051 | 304.5992 | 263.0122 | 261.6335 | 278.3968 | 252.9937 | 271.4311 | 290.4364 | 245.5415 | 255.2869 | 269.4811 | 279.7085 | 297.0573 | 285.9622 | 296.3518
BDL7NEW |  |  | Mar | 293.4515 | 279.9775 | 332.2087 | 286.4516 | 276.9686 | 282.5753 | 236.4988 | 267.7569 | 300.2128 | 243.5012 | 250.9568 | 304.8547 | 271.333 | 272.0402 | 263.1316 | 280.8168
BDL7NEW |  |  | Apr | 296.5601 | 291.8536 | 326.9202 | 281.96 | 303.9742 | 294.8418 | 254.6125 | 266.4255 | 328.2974 | 240.904 | 251.143 | 286.0058 | 247.6293 | 272.6199 | 254.8951 | 263.5116
BDL7NEW |  |  | May | 314.5112 | 316.5285 | 348.7084 | 293.3193 | 254.2648 | 345.4813 | 253.1791 | 283.6139 | 323.0693 | 253.0169 | 281.3501 | 305.4193 | 278.327 | 281.5462 | 262.8526 | 261.8923
BDL7NEW |  |  | Jun | 320.8099 | 319.3198 | 407.2703 | 303.7386 | 257.8802 | 380.4211 | 255.1489 | 317.6667 | 351.332 | 259.4225 | 306.5147 | 321.4585 | 302.1084 | 303.0565 | 274.39 | 265.9312
BDL7NEW |  |  | Jul | 313.1878 | 321.3973 | 367.9783 | 320.5334 | 260.5833 | 361.9185 | 264.2958 | 321.3891 | 350.2005 | 269.3337 | 309.6912 | 317.786 | 298.5684 | 305.72 | 285.6337 | 258.3671
BDL7NEW |  |  | Aug | 317.1632 | 326.1526 | 366.2862 | 308.6044 | 268.6801 | 335.6285 | 260.9262 | 321.413 | 305.0935 | 263.4466 | 303.1005 | 316.8882 | 299.7768 | 292.2502 | 280.348 | 251.5745
BDL7NEW |  |  | Sep | 312.3842 | 317.288 | 338.0401 | 293.8026 | 269.803 | 337.1521 | 285.5128 | 300.8343 | 314.4393 | 267.4552 | 287.1345 | 323.787 | 282.81 | 279.7194 | 266.4356 | 233.2577
BDL7NEW |  |  | Oct | 307.699 | 303.422 | 321.363 | 291.7689 | 284.6167 | 309.6748 | 258.7236 | 282.5487 | 305.8471 | 243.6981 | 272.4515 | 310.7467 | 250.5599 | 271.0477 | 252.1889 | 273.9821
BDL7NEW |  |  | Nov | 298.9814 | 292.6658 | 306.2614 | 261.5966 | 262.7198 | 275.8777 | 246.627 | 270.0528 | 279.9011 | 258.5396 | 272.21 | 289.1677 | 271.8293 | 260.9622 | 275.3091 | 283.548
BDL7NEW |  |  | Dec | 294.4665 | 284.382 | 297.8748 | 273.5122 | 278.3042 | 281.7916 | 250.5587 | 267.1821 | 272.0852 | 261.7326 | 272.1729 | 286.9749 | 277.6402 | 306.2698 | 278.9566 | 293.8406
BDL7NEW |  |  | Time of Peak Electrical Demand
BDL7NEW |  |  | Jan | 06-JAN-17:49 | 03-JAN-13:00 | 26-JAN-15:00 | 30-JAN-07:10 | 26-JAN-13:09 | 30-JAN-16:00 | 17-JAN-07:10 | 17-JAN-07:10 | 23-JAN-07:10 | 03-JAN-17:00 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-08:09 | 09-JAN-07:10 | 17-JAN-09:09
BDL7NEW |  |  | Feb | 23-FEB-11:00 | 23-FEB-14:39 | 28-FEB-17:19 | 14-FEB-07:10 | 10-FEB-10:00 | 08-FEB-17:19 | 15-FEB-17:49 | 06-FEB-07:10 | 14-FEB-14:00 | 21-FEB-17:40 | 06-FEB-09:09 | 08-FEB-17:30 | 06-FEB-07:10 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
BDL7NEW |  |  | Mar | 13-MAR-15:50 | 24-MAR-13:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-12:09 | 21-MAR-15:00 | 13-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 20-MAR-06:10 | 20-MAR-08:09 | 30-MAR-13:00 | 13-MAR-06:10 | 30-MAR-16:19 | 27-MAR-08:09 | 13-MAR-07:10
BDL7NEW |  |  | Apr | 03-APR-14:09 | 21-APR-14:00 | 26-APR-16:19 | 14-APR-16:10 | 11-APR-16:00 | 21-APR-16:19 | 13-APR-15:20 | 04-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 28-APR-16:00 | 26-APR-16:19 | 14-APR-15:00 | 06-APR-16:19 | 03-APR-08:09 | 03-APR-06:10
BDL7NEW |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:19 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-16:19 | 05-MAY-15:00 | 04-MAY-16:00 | 18-MAY-12:00 | 31-MAY-12:09 | 04-MAY-16:00 | 31-MAY-16:00 | 24-MAY-14:00
BDL7NEW |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 28-JUN-12:09 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 15-JUN-16:19
BDL7NEW |  |  | Jul | 13-JUL-14:00 | 05-JUL-15:00 | 19-JUL-16:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-16:19 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-16:19 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 13-JUL-16:40 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
BDL7NEW |  |  | Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-12:00 | 18-AUG-14:00 | 15-AUG-12:09 | 17-AUG-15:09 | 01-AUG-15:09 | 18-AUG-16:49 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 15-AUG-16:00
BDL7NEW |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 20-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:00 | 01-SEP-15:00 | 27-SEP-15:00 | 06-SEP-13:09 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 25-SEP-06:10
BDL7NEW |  |  | Oct | 06-OCT-14:30 | 06-OCT-15:00 | 02-OCT-16:00 | 12-OCT-15:00 | 30-OCT-12:00 | 03-OCT-15:00 | 30-OCT-13:30 | 20-OCT-15:09 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-16:49 | 05-OCT-15:20 | 06-OCT-14:00 | 19-OCT-16:00 | 30-OCT-06:10 | 30-OCT-08:09
BDL7NEW |  |  | Nov | 07-NOV-17:40 | 27-NOV-17:19 | 13-NOV-13:00 | 16-NOV-17:40 | 08-NOV-11:00 | 10-NOV-16:00 | 16-NOV-16:00 | 03-NOV-13:00 | 08-NOV-17:19 | 20-NOV-07:10 | 02-NOV-16:49 | 10-NOV-13:00 | 27-NOV-07:10 | 27-NOV-07:10 | 24-NOV-07:10 | 06-NOV-08:09
BDL7NEW |  |  | Dec | 15-DEC-17:30 | 19-DEC-17:30 | 06-DEC-17:19 | 18-DEC-07:10 | 18-DEC-10:00 | 05-DEC-16:30 | 29-DEC-16:00 | 26-DEC-07:10 | 18-DEC-07:10 | 11-DEC-07:10 | 26-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 21-DEC-07:10 | 29-DEC-09:09
BDL7NEW |  | Source Energy
BDL7NEW |  |  | Total Source Energy (GJ) | 21095.52 | 22432.3 | 20452.48 | 20391.87 | 17537.77 | 22196.98 | 17145.66 | 21596.69 | 20482.3 | 11356.13 | 20881.5 | 19995.66 | 20786.48 | 20626.22 | 20496.26 | 21813.14
BDL7NEW |  |  | Total Source Energy (MJ/m2) | 5545.6 | 5897.02 | 5376.56 | 5360.63 | 4610.34 | 5835.15 | 4507.26 | 5677.35 | 5384.4 | 2985.31 | 5489.34 | 5256.47 | 5464.36 | 5422.23 | 5388.07 | 5734.25
BDL7NEW |  | Water Consumption (m3)
BDL7NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Humidification | 1.33 | 22.14 | 86.45 | 65.27 | 22.31 | 184.82 | 12.91 | 105.85 | 206.54 | 41.71 | 125.05 | 213.16 | 159.43 | 205.75 | 199.11 | 251.48
BDL7NEW |  |  | Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
BDL7NEW |  |  | Total Building | 241.81 | 262.62 | 326.93 | 305.75 | 262.79 | 425.3 | 253.38 | 346.33 | 447.02 | 282.19 | 365.53 | 453.64 | 399.9 | 446.23 | 439.59 | 491.96
BDL7NEW |  | Emissions
BDL7NEW |  |  | Carbon Equivalent (kg) | 467991.173 | 545813.231 | 512085.8148 | 489723.5028 | 203364.2802 | 553358.7084 | 201115.5855 | 437359.0577 | 645329.9334 | 149390.2295 | 781796.8792 | 627078.7363 | 532682.9101 | 557726.3962 | 523479.7563 | 453034.5754
BDL7NEW |  |  | CO2 (kg) | 1107880 | 1388050 | 1231020 | 1144680 | 554621.6581 | 1335530 | 549738.8098 | 1017640 | 1532470 | 385173.2744 | 1838190 | 1490780 | 1264660 | 1329910 | 1244460 | 1163560
BDL7NEW |  |  | NOX (kg) | 1849.4601 | 1767.4302 | 1968.1418 | 2051.9524 | 482.6407 | 2089.0612 | 479.2311 | 1854.9794 | 2562.8269 | 499.7793 | 3191.3499 | 2486.0108 | 2141.6025 | 2215.2164 | 2100.1305 | 1383.2714
BDL7NEW |  |  | SO2 (kg) | 6645.7637 | 7111.6096 | 6159.1607 | 4970.354 | 3739.4097 | 8246.0825 | 3556.2763 | 5146.3396 | 6348.8858 | 960.297 | 9136.5376 | 6137.749 | 3241.3506 | 3651.655 | 3165.9256 | 6845.3972
BDL7NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDL7NEW |  |  | Hg (kg) | 0.0305 | 0.0203 | 0.017 | 0.0185 | 0.002 | 0.0157 | 0.0019 | 0.0211 | 0.025 | 0.0041 | 0.0279 | 0.0242 | 0.024 | 0.0257 | 0.0235 | 0.0236
BDL7NEW |  |  | Water for Electricity (m3) | 822.4264 | 2425.63 | 45491.9 | 8839.86 | 22558.2 | 41121.9 | 21452.8 | 320.0253 | 6601.07 | 12682 | 2103.13 | 6381.49 | 2130.07 | 86609 | 2080.48 | 1373.7

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | 12.29 | 71.86 | 3666.11
[5 empty] | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 6.41
[5 empty] | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
| Sun |  |  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
| Sun |  |  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | INFIL_SCH | Fraction | Through 12/31 | SummerDesign, WinterDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
[5 empty] | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  | RADIOLOGY_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 11.64 | 70.08 | 3654.17
[5 empty] | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
|  | OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
|  | OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
| Sat |  |  |  | Sat, WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
| Sun |  |  |  | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
| Sat |  |  |  | Sat, WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
| Sun |  |  |  | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
|  | AHU-1_MinOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
|  | AHU-1_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 17 | 102 | 5151
[5 empty] | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AHU-2_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
[5 empty] | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
|  | CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
|  | HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
|  | HeatSys1 Loop Setpoint Sched | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
SchGas | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
| Sat |  |  |  | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
| Sun |  |  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
|  | Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600