## 1
1 | Building Summary Primary School pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 6871 | 6871 | 6871
nFloor |  | Number of Floors | 1 | 1 | 1
glazing |  | Total | 0.35 | 0.35 | 0.35
hCeiling |  | Floor to Ceiling Height (m) | 4 | 4 | 4
areaWall |  | Gross Dimensions - Total Area (m2) | 2512 | 2512 | 2512
ver2hor |  | Wall to Skin Ratio | 0.27 | 0.27 | 0.27
areaRoof |  | Gross Dimensions - Total Area (m2) | 6871 | 6871 | 6871
areaWindow |  | Total Area (m2) | 879.18 | 879.18 | 879.18

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD8PRE | Total | Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793 | 18.0685 | 16.3196 | 23.3356 | 592.4974 | 10 | 1.8156 | 12474.9726 |  | 1.3934
BLD8PST | Total | Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793 | 18.0685 | 16.3196 | 23.3356 | 592.4974 | 10 | 1.8156 | 12474.9726 |  | 1.3934
BLD8PST | Total | Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793 | 13.029 | 16.3196 | 23.3356 | 592.4974 | 10 | 1.8156 | 12474.9726 |  | 0.37157

## 3
3 | UWG | Location Summary
Building | City |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD8PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD8PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD8PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD8PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD8PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD8PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD8PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD8PRE | HVAC |  | Air Conditioning (kW) | 911.6867 | 951.7706 | 934.4092 | 916.2702 | 677.2224 | 810.9993 | 734.8399 | 865.5003 | 611.9193 | 572.7429 | 679.1079 | 477.9276 | 615.5421 | 405.8066 | 552.2387 | 465.3094
BLD8PRE | HEAT |  | Heating (kW) | 663.4141 | 849.6126 | 760.117 | 906.8188 | 644.1176 | 783.1333 | 818.3149 | 937.4709 | 744.1614 | 769.711 | 878.0812 | 692.1859 | 871.189 | 767.2065 | 831.761 | 1187.6845
BLD8PRE | COP |  | Air Conditioning (COP) | 3.2271 | 3.2021 | 3.2034 | 3.228 | 3.2558 | 3.254 | 3.2515 | 3.2507 | 3.2571 | 3.2587 | 3.2577 | 3.2661 | 3.2594 | 3.2754 | 3.2606 | 3.2775
BLD8PRE | EffHeat |  | Heating Efficiency (%) | 0.75053 | 0.7508 | 0.75025 | 0.7509 | 0.75058 | 0.7505 | 0.75005 | 0.75112 | 0.75121 | 0.75103 | 0.7532 | 0.75351 | 0.75414 | 0.75439 | 0.75475 | 0.76647
BLD8PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 38.99 | 40.71 | 42.87 | 41.39 | 36.3 | 41.42 | 45.5 | 37.52 | 37.03 | 34.16 | 29.19 | 27.98 | 26.63 | 25.55 | 24.73 | 29.95
BLD8PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD8PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD8PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD8PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD8PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD8PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD8PST | HVAC |  | Air Conditioning (kW) | 822.1905 | 686.7641 | 643.3174 | 679.6546 | 645.0202 | 558.5353 | 618.4265 | 582.8622 | 435.649 | 433.2462 | 556.1259 | 388.9968 | 499.246 | 355.2969 | 483.0476 | 385.2013
BLD8PST | HEAT |  | Heating (kW) | 605.1958 | 658.4098 | 536.0416 | 696.7849 | 611.1773 | 533.8775 | 734.4243 | 676.3842 | 541.2077 | 581.0039 | 749.8306 | 563.1595 | 742.7972 | 687.1379 | 737.61 | 1039.3861
BLD8PST | COP |  | Air Conditioning (COP) | 3.2514 | 3.2575 | 3.2585 | 3.258 | 3.2565 | 3.2614 | 3.2542 | 3.2608 | 3.2677 | 3.2643 | 3.2619 | 3.2947 | 3.2648 | 3.2904 | 3.2642 | 3.3112
BLD8PST | EffHeat |  | Heating Efficiency (%) | 0.72429 | 0.72789 | 0.72854 | 0.72857 | 0.72459 | 0.7303 | 0.72449 | 0.73186 | 0.73162 | 0.73114 | 0.73131 | 0.73559 | 0.73381 | 0.73281 | 0.73401 | 0.72988
BLD8PST | Fan |  | Fan Max Flow Rate (m3/s ) | 34.96 | 29.49 | 27.75 | 29.3 | 34.13 | 25.79 | 38.14 | 25.32 | 25.33 | 24.81 | 24.23 | 21.9 | 21.95 | 22.52 | 21.29 | 25.12
BLD8NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD8NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BLD8NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD8NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD8NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD8NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD8NEW | HVAC |  | Air Conditioning (kW) | 575.968 | 590.1967 | 592.1855 | 550.0136 | 436.4604 | 501.0436 | 535.5038 | 559.0367 | 410.6226 | 379.3659 | 529.5895 | 384.29 | 515.2505 | 336.3166 | 475.6128 | 288.3576
BLD8NEW | HEAT |  | Heating (kW) | 451.4675 | 582.725 | 501.3631 | 586.7039 | 397.948 | 478.1787 | 646.2082 | 655.4372 | 510.1186 | 511.352 | 722.8907 | 560.197 | 761.0452 | 662.5286 | 738.6563 | 821.8783
BLD8NEW | COP |  | Air Conditioning (COP) | 3.2628 | 3.2622 | 3.2612 | 3.2641 | 3.2697 | 3.265 | 3.2633 | 3.2637 | 3.2842 | 3.2941 | 3.2646 | 3.2973 | 3.2649 | 3.294 | 3.2673 | 3.3392
BLD8NEW | EffHeat |  | Heating Efficiency (%) | 0.76347 | 0.76374 | 0.76332 | 0.76461 | 0.76517 | 0.76472 | 0.76208 | 0.76246 | 0.76489 | 0.76523 | 0.76306 | 0.7658 | 0.7633 | 0.76359 | 0.76374 | 0.76439
BLD8NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 25.04 | 25.62 | 25.69 | 23.99 | 20.92 | 22.63 | 32.59 | 24.36 | 23.6 | 21.28 | 23.17 | 21.63 | 22.59 | 21.27 | 21.21 | 19.26

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip1 | WD | BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69 | 3348.11
| Sat |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
| Sun |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
SchLight1 | WD | BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87 | 3466.2
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchOcc1 | WD | BLDG_OCC_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75 | 1543.82
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool1 | WD | CLGSETP_SCH | Temperature | Through 6/30 | SummerDesign | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 576 | 1296 | 67577.14
| Sat |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 603
| Sun |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
SetHeat1 | WD | HTGSETP_SCH | Temperature | Through 6/30 | WinterDesign | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 504 | 768 | 40045.71
| Sat |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 459
| Sun |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
SchGas1 | WD | KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 6.91 | 35.35 | 1646.6
| Sat |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.8
| Sun |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.8
SchSWH1 | WD | BLDG_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
| Sun |  |  |  | Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
SchEquip2 | WD | BLDG_EQUIP_SCH |  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 41.25
| Sat |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
| Sun |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchLight2 | WD | BLDG_LIGHT_SCH |  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 40.64
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchOcc2 | WD | BLDG_OCC_SCH |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool2 | WD | CLGSETP_SCH |  | Through 9/1 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
| Sat |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27
| Sun |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 615
SetHeat2 | WD | HTGSETP_SCH |  | Through 9/1 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
| Sat |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 439
| Sun |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16
SchGas2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 2.54 | 13.5
| Sat |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.8
| Sun |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.84
note: Schedule 2 is for summer break

## BuildingSummary
1 | Building Summary Primary School pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Primary School Reference Building new construction 90.1-2004 | Primary School Reference Building new construction 90.1-2004 | Primary School Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Education | Education | Education
Form
areaFloor |  | Total Floor Area (m2) | 6871 | 6871 | 6871
|  | Building Shape | "E" Shape | "E" Shape | "E" Shape
Aspect Ratio
nFloor |  | Number of Floors | 1 | 1 | 1
Window Fraction (Window to Wall Ratio)
|  | South | 0.35 | 0.35 | 0.35
|  | East | 0.35 | 0.35 | 0.35
|  | North | 0.35 | 0.35 | 0.35
|  | West | 0.35 | 0.35 | 0.35
glazing |  | Total | 0.35 | 0.35 | 0.35
|  | Skylight/TDD Percentage |  |  | 0.19%
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | See pictures | See pictures | See pictures
hCeiling |  | Floor to Ceiling Height (m) | 4 | 4 | 4
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed
areaWall |  | Gross Dimensions - Total Area (m2) | 2512 | 2512 | 2512
|  | Net Dimensions - Total Area (m2) | 1619.42 | 1619.42 | 1619.42
ver2hor |  | Wall to Skin Ratio | 0.27 | 0.27 | 0.27
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 6871 | 6871 | 6871
|  | Net Dimensions - Total Area (m2) | 6871 | 6871 | 6871
|  | Roof to Skin Ratio | 0.73 | 0.73 | 0.73
Window Dimensions (m2)
|  | South | 324.79 | 324.79 | 324.79
|  | East | 114.8 | 114.8 | 114.8
|  | North | 324.79 | 324.79 | 324.79
|  | West | 114.8 | 114.8 | 114.8
areaWindow |  | Total Area (m2) | 879.18 | 879.18 | 879.18
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) |  |  | 13.38
|  | Operable area (m2) |  |  | 0
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
|  | Dimensions - Total Area (m2) | 6871 | 6871 | 6871
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 2932 | 2932 | 2932
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 13742 | 13742 | 13742
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 1.3934 | 1.3934 | 0.37
HVAC
|  | System Type | CAV, PSZ-AC (gym, kitchen, & cafeteria) | CAV, PSZ-AC (gym, kitchen, & cafeteria) | CAV, PSZ-AC (gym, kitchen, & cafeteria)
|  | Heating Type | gas boiler, gas furnace (gym, kitchen, & cafeteria) | gas boiler, gas furnace (gym, kitchen, & cafeteria) | gas boiler, gas furnace (gym, kitchen, & cafeteria)
|  | Cooling Type | PACU | PACU | PACU
|  | Fan Control | Constant | Constant | Constant
Service Water Heating
|  | SWH Type | Storage Tank | Storage Tank | Storage Tank
|  | Fuel | Natural Gas | Natural Gas | Natural Gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 971.75 | 971.75 | 971.75

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 21.5278 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140.0001 | 49 | 4 | 78.75 | 21.5278 | 15 |  |  | 8 |  | 630 |  | 1.4738
|  | COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72.0001 | 25.2 | 3.33 | 48.6486 | 21.5278 | 20 |  |  | 8 |  | 389.1892 |  | 1.4738
|  | MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 |  | 0 | 11.1486 | 4 |  |  |  | 0.5 | 273 |  | 1.0876
|  | LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76.0001 | 26.6 |  | 0 | 12.2682 | 4 |  |  |  | 0.5 | 85.5 |  | 1.4738
|  | MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 8.263 | 4 |  |  |  | 0.25 | 63 |  | 1.0203
|  | BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 10 | 19 | 9.7047 | 4 |  | 213.9574 | 25 |  | 300 | 283.1682 | 1.2352
|  | OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168.0002 | 58.8001 | 20 | 22.05 | 20.3418 | 10.8 |  |  | 10 |  | 220.5 |  | 1.409
|  | GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68.0001 | 37.18 | 3.33 | 107.2072 | 11.4717 | 5 |  |  | 10 |  | 1072.0721 |  | 1.2147
|  | KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 17.2091 | 190.521 | 954.3991 | 378.54 | 8 |  | 201.4993 | 1557.4251 | 1.2147
|  | CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144.0001 | 50.4 | 1.3935 | 226.0419 | 15.0583 | 25.4028 |  |  | 10 |  | 2260.419 |  | 1.4868
|  | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160.0001 | 56.0001 | 4.35 | 91.7241 | 22.7584 | 15 |  |  | 8 |  | 733.7931 |  | 1.4295
BLD8PRE | Total | Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793 | 18.0685 | 16.3196 | 23.3356 | 592.4974 |  | 1.8156 | 12474.9726 |  | 1.3934
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 21.5278 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140.0001 | 49 | 4 | 78.75 | 21.5278 | 15 |  |  | 8 |  | 630 |  | 1.4738
|  | COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72.0001 | 25.2 | 3.33 | 48.6486 | 21.5278 | 20 |  |  | 8 |  | 389.1892 |  | 1.4738
|  | MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 |  | 0 | 11.1486 | 4 |  |  |  | 0.5 | 273 |  | 1.0876
|  | LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76.0001 | 26.6 |  | 0 | 12.2682 | 4 |  |  |  | 0.5 | 85.5 |  | 1.4738
|  | MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 8.263 | 4 |  |  |  | 0.25 | 63 |  | 1.0203
|  | BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 10 | 19 | 9.7047 | 4 |  | 213.9574 | 25 |  | 300 | 283.1682 | 1.2352
|  | OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168.0002 | 58.8001 | 20 | 22.05 | 20.3418 | 10.8 |  |  | 10 |  | 220.5 |  | 1.409
|  | GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68.0001 | 37.18 | 3.33 | 107.2072 | 11.4717 | 5 |  |  | 10 |  | 1072.0721 |  | 1.2147
|  | KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 17.2091 | 190.521 | 954.3991 | 378.54 | 8 |  | 201.4993 | 1557.4251 | 1.2147
|  | CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144.0001 | 50.4 | 1.3935 | 226.0419 | 15.0583 | 25.4028 |  |  | 10 |  | 2260.419 |  | 1.4868
|  | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160.0001 | 56.0001 | 4.35 | 91.7241 | 22.7584 | 15 |  |  | 8 |  | 733.7931 |  | 1.4295
BLD8PST | Total | Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793 | 18.0685 | 16.3196 | 23.3356 | 592.4974 |  | 1.8156 | 12474.9726 |  | 1.3934
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 15 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 15 |  |  | 8 |  | 954 |  | 0.39302
|  | CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.3819 | 4 |  |  |  | 0.5 | 96 |  | 0.2891
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 15 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 15 |  |  | 8 |  | 954 |  | 0.39302
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 15 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 15 |  |  | 8 |  | 954 |  | 0.39302
|  | CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.3819 | 4 |  |  |  | 0.5 | 96 |  | 0.2891
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 15 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 15 |  |  | 8 |  | 954 |  | 0.39302
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 15 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 15 |  |  | 8 |  | 954 |  | 0.39302
|  | CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.3819 | 4 |  |  |  | 0.5 | 96 |  | 0.2891
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 15 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140.0001 | 49 | 4 | 78.75 | 15.0695 | 15 |  |  | 8 |  | 630 |  | 0.39302
|  | COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72.0001 | 25.2 | 3.33 | 48.6486 | 15.0695 | 20 |  |  | 8 |  | 389.1892 |  | 0.39302
|  | MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 273 |  | 0.29003
|  | LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76.0001 | 26.6 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 85.5 |  | 0.39302
|  | MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 16.1458 | 4 |  |  |  | 0.25 | 63 |  | 0.27209
|  | BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 10 | 19 | 9.6875 | 4 |  | 213.9574 | 25 |  | 300 | 283.1682 | 0.32937
|  | OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168.0002 | 58.8001 | 20 | 22.05 | 11.8403 | 10.8 |  |  | 10 |  | 220.5 |  | 0.37575
|  | GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68.0001 | 37.18 | 3.33 | 107.2072 | 15.0695 | 5 |  |  | 10 |  | 1072.0721 |  | 0.32392
|  | KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 12.9167 | 190.521 | 954.3991 | 378.54 | 8 |  | 201.4993 | 1557.4251 | 0.32392
|  | CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144.0001 | 50.4 | 1.3935 | 226.0419 | 15.0695 | 25.4028 |  |  | 10 |  | 2260.419 |  | 0.39648
|  | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160.0001 | 56.0001 | 4.35 | 91.7241 | 13.9931 | 15 |  |  | 8 |  | 733.7931 |  | 0.3812
BLD8PST | Total | Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793 | 13.029 | 16.3196 | 23.3356 | 592.4974 |  | 1.8156 | 12474.9726 |  | 0.37157

## LocationSummary
3 | UWG | Location Summary
Building | City |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD8PRE |  | Program
BLD8PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD8PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD8PRE |  |  | Weighting Factor
BLD8PRE |  | Fabric
BLD8PRE |  |  | Exterior walls
BLD8PRE | TypeWall |  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
BLD8PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD8PRE |  |  | Roof
BLD8PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD8PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD8PRE |  |  | Window
BLD8PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD8PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD8PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD8PRE |  |  | Skylights/TDD
BLD8PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD8PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD8PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD8PRE |  |  | Foundation
BLD8PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD8PRE |  |  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
BLD8PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD8PRE |  | HVAC
BLD8PRE |  |  | HVAC Sizing
BLD8PRE | HVAC |  | Air Conditioning (kW) | 911.6867 | 951.7706 | 934.4092 | 916.2702 | 677.2224 | 810.9993 | 734.8399 | 865.5003 | 611.9193 | 572.7429 | 679.1079 | 477.9276 | 615.5421 | 405.8066 | 552.2387 | 465.3094
BLD8PRE |  |  | PSZ-AC_1:6_COOLC DXCOIL | 23.7298 | 23.907 | 24.013 | 24.285 | 20.4005 | 23.0141 | 22.2256 | 20.8771 | 19.8219 | 14.6556 | 17.4512 | 15.7767 | 15.8131 | 11.3264 | 13.1649 | 9.453
BLD8PRE |  |  | PSZ-AC_2:5_COOLC DXCOIL | 35.7862 | 36.9549 | 36.9685 | 36.7607 | 29.6633 | 34.6212 | 24.9487 | 31.0078 | 27.9426 | 23.8625 | 26.6221 | 24.2671 | 26.6221 | 19.8621 | 26.6221 | 17.7466
BLD8PRE |  |  | PSZ-AC_2:7_COOLC DXCOIL | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 43.4953 | 56.2748 | 52.9305 | 50.5807 | 56.2748 | 53.3823 | 56.2748 | 46.2592 | 56.2748 | 37.5134
BLD8PRE |  |  | VAV_OTHER_COOLC DXCOIL | 226.7553 | 235.2684 | 223.308 | 220.6536 | 156.1768 | 189.4095 | 162.1376 | 205.1684 | 144.5948 | 123.4632 | 164.7861 | 105.8498 | 142.77 | 97.775 | 133.2272 | 118.8603
BLD8PRE |  |  | VAV_POD_1_COOLC DXCOIL | 222.1639 | 233.6535 | 229.2043 | 222.872 | 160.4206 | 196.6956 | 186.6485 | 214.2866 | 143.1021 | 140.154 | 161.6169 | 108.0409 | 146.3571 | 89.557 | 123.6643 | 109.0937
BLD8PRE |  |  | VAV_POD_2_COOLC DXCOIL | 170.0237 | 178.9304 | 181.2701 | 176.8794 | 124.8697 | 153.6961 | 143.3961 | 165.7977 | 108.8007 | 106.3532 | 123.2756 | 84.2261 | 110.7016 | 69.3394 | 101.2031 | 86.2975
BLD8PRE |  |  | VAV_POD_3_COOLC DXCOIL | 176.953 | 186.7815 | 183.3705 | 178.5447 | 129.4167 | 157.288 | 151.9881 | 172.0879 | 114.7268 | 113.6737 | 129.0812 | 86.3847 | 117.0034 | 71.6874 | 98.0822 | 86.3449
BLD8PRE | HEAT |  | Heating (kW) | 663.4141 | 849.6126 | 760.117 | 906.8188 | 644.1176 | 783.1333 | 818.3149 | 937.4709 | 744.1614 | 769.711 | 878.0812 | 692.1859 | 871.189 | 767.2065 | 831.761 | 1187.6845
BLD8PRE |  |  | HEATSYS1 BOILER | 488.6898 | 620.2554 | 565.2652 | 659.8001 | 473.8132 | 577.4734 | 612.7455 | 676.9464 | 535.5992 | 557.4208 | 588.3454 | 458.3767 | 563.1811 | 491.1881 | 524.9497 | 803.7291
BLD8PRE |  |  | PSZ-AC_1:6_HEATC | 36.9969 | 49.2058 | 41.6987 | 53.9194 | 33.0798 | 43.2021 | 50.7541 | 51.5993 | 41.9316 | 35.1029 | 50.387 | 39.4812 | 49.3422 | 40.3112 | 42.0473 | 56.0867
BLD8PRE |  |  | PSZ-AC_2:5_HEATC | 49.9899 | 64.3258 | 55.4316 | 68.1532 | 45.9737 | 56.8183 | 53.9531 | 69.8379 | 56.118 | 56.9032 | 76.8662 | 62.4079 | 83.0697 | 75.6966 | 85.0282 | 105.2941
BLD8PRE |  |  | PSZ-AC_2:7_HEATC | 87.7376 | 115.8256 | 97.7215 | 124.946 | 91.2508 | 105.6395 | 100.8623 | 139.0873 | 110.5125 | 120.2841 | 162.4826 | 131.9201 | 175.596 | 160.0105 | 179.7358 | 222.5747
BLD8PRE |  |  | HVAC Efficiency
BLD8PRE | COP |  | Air Conditioning (COP) | 3.2271 | 3.2021 | 3.2034 | 3.228 | 3.2558 | 3.254 | 3.2515 | 3.2507 | 3.2571 | 3.2587 | 3.2577 | 3.2661 | 3.2594 | 3.2754 | 3.2606 | 3.2775
BLD8PRE |  |  | PSZ-AC_1:6_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD8PRE |  |  | PSZ-AC_2:5_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67
BLD8PRE |  |  | PSZ-AC_2:7_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.5
BLD8PRE |  |  | VAV_OTHER_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD8PRE |  |  | VAV_POD_1_COOLC DXCOIL | 3.23 | 3.13 | 3.13 | 3.13 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD8PRE |  |  | VAV_POD_2_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23
BLD8PRE |  |  | VAV_POD_3_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD8PRE | EffHeat |  | Heating Efficiency (%) | 0.75053 | 0.7508 | 0.75025 | 0.7509 | 0.75058 | 0.7505 | 0.75005 | 0.75112 | 0.75121 | 0.75103 | 0.7532 | 0.75351 | 0.75414 | 0.75439 | 0.75475 | 0.76647
BLD8PRE |  |  | HEATSYS1 BOILER | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.76
BLD8PRE |  |  | PSZ-AC_1:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD8PRE |  |  | PSZ-AC_2:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD8PRE |  |  | PSZ-AC_2:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD8PRE |  |  | HVAC Control - Economizer
BLD8PRE |  |  | PSZ-AC_1:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD8PRE |  |  | PSZ-AC_2:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD8PRE |  |  | PSZ-AC_2:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
BLD8PRE |  |  | VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PRE |  |  | VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PRE |  |  | VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PRE |  |  | VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 38.99 | 40.71 | 42.87 | 41.39 | 36.3 | 41.42 | 45.5 | 37.52 | 37.03 | 34.16 | 29.19 | 27.98 | 26.63 | 25.55 | 24.73 | 29.95
BLD8PRE |  |  | BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
BLD8PRE |  |  | CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD8PRE |  |  | KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
BLD8PRE |  |  | PSZ-AC_1:6_FAN | 0.96 | 0.96 | 0.97 | 0.98 | 0.82 | 0.93 | 1.14 | 0.84 | 0.86 | 0.66 | 0.7 | 0.68 | 0.64 | 0.57 | 0.53 | 0.57
BLD8PRE |  |  | PSZ-AC_2:5_FAN | 1.44 | 1.49 | 1.49 | 1.48 | 1.19 | 1.39 | 1.34 | 1.25 | 1.27 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07
BLD8PRE |  |  | PSZ-AC_2:7_FAN | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
BLD8PRE |  |  | VAV_OTHER_FAN | 9.55 | 10.01 | 10.32 | 10.12 | 8.5 | 9.77 | 9.79 | 8.83 | 8.73 | 7.28 | 6.64 | 6.29 | 5.75 | 5.91 | 5.71 | 7.18
BLD8PRE |  |  | VAV_POD_1_FAN | 8.95 | 9.41 | 10.13 | 9.61 | 8.44 | 9.85 | 11.28 | 8.75 | 8.64 | 8.23 | 6.51 | 6.2 | 5.89 | 5.41 | 5.15 | 6.59
BLD8PRE |  |  | VAV_POD_2_FAN | 6.85 | 7.21 | 7.74 | 7.38 | 6.4 | 7.47 | 8.66 | 6.68 | 6.49 | 6.11 | 4.96 | 4.68 | 4.46 | 4.15 | 4.08 | 5.21
BLD8PRE |  |  | VAV_POD_3_FAN | 7.13 | 7.52 | 8.11 | 7.71 | 6.84 | 7.9 | 9.18 | 7.06 | 6.93 | 6.7 | 5.2 | 4.95 | 4.71 | 4.33 | 4.08 | 5.22
BLD8PRE |  | Utility Costs
BLD8PRE |  |  | Electric Utility Rates
BLD8PRE |  |  | Average Annual Rate ($/kWh) | 0.090517 | 0.12236 | 0.093434 | 0.097314 | 0.13078 | 0.10168 | 0.14747 | 0.078833 | 0.037098 | 0.075483 | 0.088923 | 0.037112 | 0.060847 | 0.076329 | 0.059081 | 0.094584
BLD8PRE |  |  | Total Cost ($/m2) | 19.51 | 24.2 | 19.37 | 17.16 | 21.26 | 19.4 | 22.2 | 13.15 | 6.13 | 11.08 | 13.79 | 5.64 | 9.21 | 11.15 | 8.52 | 13.59
BLD8PRE |  |  | Gas Utility Rates
BLD8PRE |  |  | Average Annual Rate ($/MJ) | 0.011441 | 0.0081017 | 0.008362 | 0.0098226 | 0.0084927 | 0.0078004 | 0.0085246 | 0.0097213 | 0.0069388 | 0.0084051 | 0.0083799 | 0.0069552 | 0.0078906 | 0.0081588 | 0.0078765 | 0.0041241
BLD8PRE |  |  | Total Cost ($/m2) | 0.66 | 1.19 | 1.01 | 2.43 | 0.9 | 1.32 | 1.71 | 3.86 | 1.94 | 2.97 | 3.68 | 2.32 | 4.36 | 3.62 | 5.15 | 4.94
BLD8PRE |  |  | Total Utility Costs
BLD8PRE |  |  | Cost Intensity ($/m2) | 20.17 | 25.39 | 20.38 | 19.59 | 22.16 | 20.72 | 23.91 | 17.01 | 8.07 | 14.05 | 17.47 | 7.96 | 13.58 | 14.77 | 13.67 | 18.52
BLD8PRE |  | Energy - End Uses
BLD8PRE |  |  | Electricity (kWh)
BLD8PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Cooling | 485038.8889 | 372450 | 424077.7778 | 230688.8889 | 143869.4444 | 314661.1111 | 65438.8889 | 169711.1111 | 146372.2222 | 44233.3333 | 98194.4444 | 74763.8889 | 74913.8889 | 41102.7778 | 29144.4444 | 16302.7778
BLD8PRE |  |  | Interior Lighting | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556
BLD8PRE |  |  | Exterior Lighting | 45977.7778 | 45961.1111 | 45952.7778 | 45944.4444 | 45911.1111 | 45900 | 45925 | 45897.2222 | 45913.8889 | 45822.2222 | 45902.7778 | 45877.7778 | 45872.2222 | 45863.8889 | 45836.1111 | 45555.5556
BLD8PRE |  |  | Interior Equipment | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556
BLD8PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans | 72625 | 63588.8889 | 77569.4444 | 58922.2222 | 51191.6667 | 74219.4444 | 47688.8889 | 54502.7778 | 66925 | 43800 | 45625 | 47897.2222 | 43838.8889 | 42013.8889 | 40738.8889 | 47894.4444
BLD8PRE |  |  | Pumps | 11.1111 | 200 | 141.6667 | 425 | 83.3333 | 263.8889 | 247.2222 | 755.5556 | 533.3333 | 544.4444 | 825 | 711.1111 | 1302.7778 | 994.4444 | 1700 | 4091.6667
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Refrigeration | 21808.3333 | 20800 | 20780.5556 | 19850 | 19900 | 20105.5556 | 19016.6667 | 19205.5556 | 19200 | 18588.8889 | 18775 | 18661.1111 | 18552.7778 | 18213.8889 | 17836.1111 | 17238.8889
BLD8PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 1481325 | 1358863.8889 | 1424383.3333 | 1211694.4444 | 1116816.6667 | 1311011.1111 | 1034180.5556 | 1145930.5556 | 1134805.5556 | 1008855.5556 | 1065188.8889 | 1043769.4444 | 1040344.4444 | 1004047.2222 | 991116.6667 | 986944.4444
BLD8PRE |  |  | Gas (MJ)
BLD8PRE |  |  | Heating | 52120 | 644860 | 472920 | 1314750 | 345730 | 792630 | 980530 | 2324020 | 1524620 | 2016860 | 2601350 | 1877390 | 3367150 | 2611620 | 4039250 | 7749080
BLD8PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Equipment | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340
BLD8PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 108190 | 131560 | 120000 | 152910 | 146720 | 135570 | 164840 | 169830 | 166590 | 176720 | 184380 | 183230 | 197210 | 198780 | 217030 | 240670
BLD8PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 394660 | 1010770 | 827260 | 1702000 | 726790 | 1162540 | 1379710 | 2728190 | 1925550 | 2427920 | 3020060 | 2294970 | 3798700 | 3044740 | 4490620 | 8224090
BLD8PRE |  |  | Purchased Cooling (MJ)
BLD8PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Purchased Heating (MJ)
BLD8PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total Building (MJ) | 5727420 | 5902670 | 5955040 | 6064110 | 4747330 | 5882180 | 5102760 | 6853540 | 6010860 | 6059790 | 6854740 | 6052540 | 7543940 | 6659310 | 8058640 | 11777090
BLD8PRE |  | Energy - End Use Intensities
BLD8PRE |  |  | Electricity (MJ/m2)
BLD8PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Cooling (elec) | 254.1319 | 195.1419 | 222.1918 | 120.8674 | 75.3791 | 164.8639 | 34.2861 | 88.9186 | 76.6904 | 23.1757 | 51.4481 | 39.1719 | 39.2505 | 21.5354 | 15.27 | 8.5417
BLD8PRE |  |  | Interior Lighting (elec) | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742
BLD8PRE |  |  | Exterior Lighting (elec) | 24.0897 | 24.0809 | 24.0766 | 24.0722 | 24.0547 | 24.0489 | 24.062 | 24.0474 | 24.0562 | 24.0082 | 24.0504 | 24.0373 | 24.0343 | 24.03 | 24.0154 | 23.8684
BLD8PRE |  |  | Interior Equipment (elec) | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467
BLD8PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans (elec) | 38.0512 | 33.3168 | 40.6418 | 30.8718 | 26.8214 | 38.8866 | 24.9862 | 28.5563 | 35.0648 | 22.9486 | 23.9048 | 25.0953 | 22.969 | 22.0128 | 21.3448 | 25.0939
BLD8PRE |  |  | Pumps (elec) | 0.0058216 | 0.10479 | 0.074225 | 0.22268 | 0.043662 | 0.13826 | 0.12953 | 0.39587 | 0.27944 | 0.28526 | 0.43225 | 0.37258 | 0.68258 | 0.52103 | 0.8907 | 2.1438
BLD8PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Refrigeration (elec) | 11.4263 | 10.898 | 10.8878 | 10.4002 | 10.4264 | 10.5341 | 9.9636 | 10.0626 | 10.0597 | 9.7395 | 9.837 | 9.7773 | 9.7206 | 9.543 | 9.3451 | 9.0322
BLD8PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 776.1272 | 711.9648 | 746.2931 | 634.8566 | 585.1463 | 686.8927 | 541.8498 | 600.4002 | 594.5714 | 528.581 | 558.0963 | 546.8738 | 545.0793 | 526.0617 | 519.2869 | 517.1009
BLD8PRE |  |  | Gas (MJ/m2)
BLD8PRE |  |  | Heating (gas) | 7.5855 | 93.8524 | 68.8284 | 191.3477 | 50.3173 | 115.3588 | 142.7056 | 338.2361 | 221.892 | 293.5322 | 378.5985 | 273.2339 | 490.0524 | 380.0931 | 587.8693 | 1127.7951
BLD8PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Equipment (gas) | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057
BLD8PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems (gas) | 15.7459 | 19.1471 | 17.4647 | 22.2544 | 21.3535 | 19.7308 | 23.9907 | 24.7169 | 24.2454 | 25.7197 | 26.8345 | 26.6672 | 28.7018 | 28.9303 | 31.5864 | 35.0269
BLD8PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 57.4385 | 147.1067 | 120.3988 | 247.7078 | 105.7765 | 169.1952 | 200.8019 | 397.0587 | 280.2431 | 353.3576 | 439.5372 | 334.0082 | 552.8598 | 443.1291 | 653.5613 | 1196.9277
BLD8PRE |  |  | Purchased Cooling (MJ/m2)
BLD8PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Purchased Heating (MJ/m2)
BLD8PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Total Building (MJ/m2) | 833.5643 | 859.07 | 866.6919 | 882.5659 | 690.9227 | 856.0879 | 742.6517 | 997.4589 | 874.8159 | 881.9371 | 997.6335 | 880.882 | 1097.9392 | 969.1908 | 1172.8482 | 1714.0285
BLD8PRE |  | Peak Energy Demand
BLD8PRE |  |  | Electricity Peak Demand (kW)
BLD8PRE |  |  | Jan | 394.7358 | 355.3823 | 330.5272 | 277.9895 | 348.4851 | 268.6077 | 230.545 | 233.4101 | 242.1062 | 215.7463 | 216.0253 | 236.02 | 216.5027 | 218.6218 | 215.7258 | 226.5768
BLD8PRE |  |  | Feb | 411.5044 | 369.7303 | 362.3393 | 274.8634 | 332.8291 | 295.7253 | 286.2565 | 226.2464 | 289.5797 | 232.6988 | 214.9455 | 227.947 | 212.5189 | 229.8902 | 213.3256 | 221.0583
BLD8PRE |  |  | Mar | 417.5347 | 351.1435 | 435.6577 | 326.1116 | 331.8601 | 330.1182 | 257.0597 | 296.7972 | 298.6749 | 265.3616 | 256.5341 | 284.7113 | 226.5924 | 256.4816 | 211.6368 | 220.6019
BLD8PRE |  |  | Apr | 449.0916 | 401.7001 | 453.6088 | 361.4212 | 338.6999 | 441.0034 | 301.7426 | 304.8302 | 366.3253 | 247.1285 | 265.3043 | 306.1357 | 253.8361 | 241.4515 | 229.4792 | 212.249
BLD8PRE |  |  | May | 492.3712 | 508.8251 | 523.1709 | 427.426 | 346.1175 | 490.6274 | 306.7156 | 369.9806 | 399.8143 | 312.5532 | 343.6343 | 337.2309 | 348.2136 | 292.1175 | 275.149 | 252.4776
BLD8PRE |  |  | Jun | 506.3959 | 514.2568 | 638.9197 | 480.4304 | 345.7498 | 583.3993 | 314.527 | 495.4049 | 443.5011 | 326.5619 | 431.4031 | 382.8378 | 404.5009 | 356.964 | 346.3231 | 297.5598
BLD8PRE |  |  | Jul | 343.5421 | 373.0422 | 462.5435 | 382.2145 | 225.6788 | 463.4697 | 219.3514 | 365.6794 | 354.583 | 233.6138 | 301.8338 | 288.2263 | 270.954 | 258.0709 | 238.4412 | 173.9668
BLD8PRE |  |  | Aug | 369.8326 | 379.4972 | 475.2438 | 344.9612 | 258.435 | 409.1133 | 207.5413 | 370.0545 | 326.2685 | 218.3438 | 299.1195 | 287.6645 | 272.1364 | 221.9655 | 216.8403 | 170.3023
BLD8PRE |  |  | Sep | 493.2884 | 507.2602 | 559.3312 | 459.9424 | 400.8099 | 510.1983 | 419.1422 | 439.8585 | 395.3452 | 350.568 | 370.2628 | 365.5979 | 348.299 | 306.5586 | 312.5816 | 218.9835
BLD8PRE |  |  | Oct | 475.8411 | 437.9313 | 451.2868 | 380.6811 | 378.9515 | 440.9297 | 309.4002 | 357.7174 | 359.4963 | 279.0442 | 298.1337 | 341.6398 | 268.62 | 275.1412 | 237.8396 | 218.4938
BLD8PRE |  |  | Nov | 427.7074 | 373.646 | 403.0908 | 294.3888 | 348.5163 | 310.0702 | 249.6366 | 318.3714 | 275.1979 | 228.3667 | 291.9222 | 265.067 | 243.3825 | 217.326 | 214.6404 | 222.1289
BLD8PRE |  |  | Dec | 386.4406 | 359.9942 | 310.4849 | 271.6793 | 358.8254 | 295.7515 | 234.4057 | 216.7013 | 233.3725 | 215.8036 | 215.0801 | 220.8391 | 214.9142 | 218.2163 | 214.7887 | 226.4084
BLD8PRE |  |  | Time of Peak Electrical Demand
BLD8PRE |  |  | Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:30 | 23-JAN-14:00 | 26-JAN-12:00 | 18-JAN-14:20 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 10-JAN-16:00 | 27-JAN-16:00 | 27-JAN-12:00 | 04-JAN-16:00 | 05-JAN-08:09 | 09-JAN-16:00 | 02-JAN-11:09
BLD8PRE |  |  | Feb | 23-FEB-12:00 | 23-FEB-14:00 | 28-FEB-15:39 | 27-FEB-14:00 | 13-FEB-11:00 | 27-FEB-14:39 | 14-FEB-12:00 | 15-FEB-14:50 | 14-FEB-15:00 | 21-FEB-13:00 | 01-FEB-16:00 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-08:30
BLD8PRE |  |  | Mar | 27-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-13:00 | 31-MAR-13:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-13:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 07-MAR-11:09 | 14-MAR-07:10
BLD8PRE |  |  | Apr | 03-APR-13:00 | 17-APR-14:00 | 26-APR-14:00 | 21-APR-13:00 | 13-APR-11:00 | 21-APR-14:00 | 13-APR-14:00 | 05-APR-14:00 | 21-APR-14:00 | 14-APR-13:00 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 10-APR-10:09
BLD8PRE |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-14:00 | 15-MAY-14:00 | 30-MAY-11:20 | 31-MAY-14:00 | 17-MAY-13:00 | 15-MAY-12:00 | 31-MAY-14:00 | 04-MAY-14:50 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
BLD8PRE |  |  | Jun | 27-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-13:50 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:00 | 20-JUN-13:00 | 28-JUN-13:50 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-14:00
BLD8PRE |  |  | Jul | 13-JUL-14:00 | 31-JUL-13:00 | 11-JUL-15:00 | 03-JUL-15:20 | 24-JUL-13:50 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-13:30 | 31-JUL-15:30 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:39 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD8PRE |  |  | Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:50 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-14:00 | 15-AUG-11:00 | 17-AUG-14:39 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:50 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-13:00
BLD8PRE |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-11:00 | 20-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-14:00 | 13-SEP-14:00 | 06-SEP-11:00 | 06-SEP-14:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-15:00
BLD8PRE |  |  | Oct | 06-OCT-14:50 | 13-OCT-14:00 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 30-OCT-13:30 | 12-OCT-14:50 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 27-OCT-07:19
BLD8PRE |  |  | Nov | 01-NOV-11:00 | 03-NOV-14:30 | 13-NOV-14:50 | 22-NOV-14:00 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-10:50 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 24-NOV-16:00 | 30-NOV-10:09
BLD8PRE |  |  | Dec | 14-DEC-12:00 | 19-DEC-14:00 | 11-DEC-14:00 | 01-DEC-14:39 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 20-DEC-16:00 | 05-DEC-14:00 | 14-DEC-16:19 | 13-DEC-16:19 | 21-DEC-14:30 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 29-DEC-11:09
BLD8PRE |  | Source Energy
BLD8PRE |  |  | Total Source Energy (GJ) | 18119.75 | 18871.16 | 17122.53 | 16532.7 | 13237.23 | 18151.65 | 13029.49 | 17731.43 | 15657.74 | 8978.02 | 16895.67 | 14973.73 | 17020.56 | 15889.11 | 17167.04 | 21672.03
BLD8PRE |  |  | Total Source Energy (MJ/m2) | 2637.13 | 2746.49 | 2492 | 2406.16 | 1926.54 | 2641.78 | 1896.3 | 2580.62 | 2278.82 | 1306.65 | 2458.98 | 2179.27 | 2477.16 | 2312.49 | 2498.48 | 3154.13
BLD8PRE |  | Water Consumption (m3)
BLD8PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Water Systems | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
BLD8PRE |  |  | Total Building | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
BLD8PRE |  | Emissions
BLD8PRE |  |  | Carbon Equivalent (kg) | 413369.4928 | 471490.3206 | 444903.99 | 403938.3699 | 143623.6891 | 463135.1157 | 145740.3666 | 358432.0812 | 498289.1207 | 117260.9764 | 622363.9687 | 467762.5365 | 424603.0393 | 421821.5944 | 420230.1886 | 426016.5481
BLD8PRE |  |  | CO2 (kg) | 961261.7181 | 1190030 | 1054300 | 935794.8869 | 386325.9952 | 1107860 | 394559.9085 | 835609.6165 | 1180480 | 301042.541 | 1467650 | 1113070 | 1018870 | 1012030 | 1016070 | 1124150
BLD8PRE |  |  | NOX (kg) | 1677.6911 | 1542.7754 | 1748.218 | 1716.2937 | 332.5807 | 1772.4654 | 341.3991 | 1515.5726 | 1986.2508 | 395.294 | 2528.7842 | 1851.6899 | 1677.7727 | 1658.8834 | 1639.6136 | 1260.5512
BLD8PRE |  |  | SO2 (kg) | 6340.7661 | 6482.0454 | 5727.9501 | 4253.5078 | 3249.9971 | 7211.9228 | 3009.7141 | 4183.8331 | 4955.9888 | 780.4144 | 7179.3222 | 4558.5506 | 2456.3944 | 2681.7444 | 2340.396 | 5026.1518
BLD8PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PRE |  |  | Hg (kg) | 0.0289 | 0.0183 | 0.0156 | 0.0157 | 0.0015 | 0.0136 | 0.0015 | 0.0171 | 0.0195 | 0.0033 | 0.022 | 0.018 | 0.0183 | 0.0189 | 0.0175 | 0.0179
BLD8PRE |  |  | Water for Electricity (m3) | 784.7434 | 2211.03 | 42310.4 | 7565.34 | 19608.8 | 35966.3 | 18157.9 | 260.1691 | 5152.93 | 10307.3 | 1652.57 | 4739.55 | 1614.03 | 63600.6 | 1537.66 | 1008.34
BLD8PST |  | Program
BLD8PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD8PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD8PST |  |  | Weighting Factor
BLD8PST |  | Fabric
BLD8PST |  |  | Exterior walls
BLD8PST | TypeWall |  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
BLD8PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD8PST |  |  | Roof
BLD8PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD8PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD8PST |  |  | Window
BLD8PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD8PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD8PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD8PST |  |  | Skylights/TDD
BLD8PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD8PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD8PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD8PST |  |  | Foundation
BLD8PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD8PST |  |  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
BLD8PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD8PST |  | HVAC
BLD8PST |  |  | HVAC Sizing
BLD8PST | HVAC |  | Air Conditioning (kW) | 822.1905 | 686.7641 | 643.3174 | 679.6546 | 645.0202 | 558.5353 | 618.4265 | 582.8622 | 435.649 | 433.2462 | 556.1259 | 388.9968 | 499.246 | 355.2969 | 483.0476 | 385.2013
BLD8PST |  |  | PSZ-AC_1:6_COOLC DXCOIL | 20.6228 | 17.5901 | 16.45 | 18.0015 | 19.8346 | 14.5213 | 20.6848 | 15.5445 | 14.3974 | 11.5927 | 14.994 | 12.9903 | 14.173 | 10.3667 | 12.227 | 8.143
BLD8PST |  |  | PSZ-AC_2:5_COOLC DXCOIL | 29.997 | 26.6221 | 26.6221 | 26.6352 | 28.7649 | 26.6221 | 23.4096 | 26.6221 | 23.5769 | 23.088 | 26.6221 | 23.726 | 26.6221 | 19.8621 | 26.6221 | 17.7466
BLD8PST |  |  | PSZ-AC_2:7_COOLC DXCOIL | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 43.4953 | 56.2748 | 52.9305 | 50.5807 | 56.2748 | 53.3823 | 56.2748 | 46.2592 | 56.2748 | 37.5134
BLD8PST |  |  | VAV_OTHER_COOLC DXCOIL | 204.3165 | 170.3143 | 142.9174 | 169.1058 | 149.2661 | 117.854 | 135.7533 | 138.255 | 94.0829 | 89.5037 | 127.6595 | 80.5765 | 111.1309 | 85.4363 | 116.0923 | 93.3751
BLD8PST |  |  | VAV_POD_1_COOLC DXCOIL | 200.1201 | 161.7371 | 157.6982 | 158.4524 | 150.7656 | 133.1226 | 151.3178 | 134.8075 | 97.5835 | 99.881 | 129.4345 | 85.0815 | 114.1599 | 74.7423 | 105.6173 | 88.824
BLD8PST |  |  | VAV_POD_2_COOLC DXCOIL | 152.2777 | 125.2762 | 118.3557 | 124.324 | 118.4662 | 104.0521 | 120.7882 | 103.8385 | 75.4804 | 77.5657 | 98.225 | 65.654 | 86.1378 | 59.5053 | 82.9336 | 69.6388
BLD8PST |  |  | VAV_POD_3_COOLC DXCOIL | 158.5816 | 128.9495 | 124.9991 | 126.861 | 121.6479 | 106.0884 | 122.9775 | 107.5197 | 77.5975 | 81.0344 | 102.9159 | 67.5861 | 90.7476 | 59.1248 | 83.2805 | 69.9603
BLD8PST | HEAT |  | Heating (kW) | 605.1958 | 658.4098 | 536.0416 | 696.7849 | 611.1773 | 533.8775 | 734.4243 | 676.3842 | 541.2077 | 581.0039 | 749.8306 | 563.1595 | 742.7972 | 687.1379 | 737.61 | 1039.3861
BLD8PST |  |  | HEATSYS1 BOILER | 440.6749 | 451.5861 | 363.5252 | 472.7502 | 442.6193 | 351.0033 | 534.3729 | 433.0791 | 347.9582 | 376.0501 | 467.1894 | 336.3233 | 439.9072 | 414.5351 | 433.7942 | 663.2031
BLD8PST |  |  | PSZ-AC_1:6_HEATC | 32.1528 | 36.2041 | 28.5655 | 39.9685 | 32.1622 | 27.2595 | 47.2356 | 38.4193 | 30.4566 | 27.7666 | 43.2924 | 32.5083 | 44.2243 | 36.8957 | 39.0518 | 48.3142
BLD8PST |  |  | PSZ-AC_2:5_HEATC | 44.6306 | 54.794 | 46.2294 | 59.1202 | 45.145 | 49.9752 | 51.9535 | 65.7984 | 52.2805 | 56.9032 | 76.8662 | 62.4079 | 83.0697 | 75.6966 | 85.0282 | 105.2941
BLD8PST |  |  | PSZ-AC_2:7_HEATC | 87.7376 | 115.8256 | 97.7215 | 124.946 | 91.2508 | 105.6395 | 100.8623 | 139.0873 | 110.5125 | 120.2841 | 162.4826 | 131.9201 | 175.596 | 160.0105 | 179.7358 | 222.5747
BLD8PST |  |  | HVAC Efficiency
BLD8PST | COP |  | Air Conditioning (COP) | 3.2514 | 3.2575 | 3.2585 | 3.258 | 3.2565 | 3.2614 | 3.2542 | 3.2608 | 3.2677 | 3.2643 | 3.2619 | 3.2947 | 3.2648 | 3.2904 | 3.2642 | 3.3112
BLD8PST |  |  | PSZ-AC_1:6_COOLC DXCOIL | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD8PST |  |  | PSZ-AC_2:5_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67
BLD8PST |  |  | PSZ-AC_2:7_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.5
BLD8PST |  |  | VAV_OTHER_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD8PST |  |  | VAV_POD_1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD8PST |  |  | VAV_POD_2_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
BLD8PST |  |  | VAV_POD_3_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
BLD8PST | EffHeat |  | Heating Efficiency (%) | 0.72429 | 0.72789 | 0.72854 | 0.72857 | 0.72459 | 0.7303 | 0.72449 | 0.73186 | 0.73162 | 0.73114 | 0.73131 | 0.73559 | 0.73381 | 0.73281 | 0.73401 | 0.72988
BLD8PST |  |  | HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD8PST |  |  | PSZ-AC_1:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD8PST |  |  | PSZ-AC_2:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
BLD8PST |  |  | PSZ-AC_2:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD8PST |  |  | HVAC Control - Economizer
BLD8PST |  |  | PSZ-AC_1:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD8PST |  |  | PSZ-AC_2:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD8PST |  |  | PSZ-AC_2:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
BLD8PST |  |  | VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PST |  |  | VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PST |  |  | VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PST |  |  | VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8PST | Fan |  | Fan Max Flow Rate (m3/s ) | 34.96 | 29.49 | 27.75 | 29.3 | 34.13 | 25.79 | 38.14 | 25.32 | 25.33 | 24.81 | 24.23 | 21.9 | 21.95 | 22.52 | 21.29 | 25.12
BLD8PST |  |  | BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
BLD8PST |  |  | CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD8PST |  |  | KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
BLD8PST |  |  | PSZ-AC_1:6_FAN | 0.83 | 0.71 | 0.66 | 0.72 | 0.8 | 0.58 | 1.06 | 0.63 | 0.62 | 0.52 | 0.6 | 0.56 | 0.57 | 0.52 | 0.49 | 0.49
BLD8PST |  |  | PSZ-AC_2:5_FAN | 1.21 | 1.07 | 1.07 | 1.07 | 1.16 | 1.07 | 1.26 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07
BLD8PST |  |  | PSZ-AC_2:7_FAN | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
BLD8PST |  |  | VAV_OTHER_FAN | 8.23 | 6.86 | 5.76 | 6.9 | 8.02 | 5.22 | 8.17 | 5.57 | 5.49 | 4.98 | 5.14 | 4.48 | 4.48 | 5.16 | 4.68 | 5.64
BLD8PST |  |  | VAV_POD_1_FAN | 8.06 | 6.51 | 6.35 | 6.38 | 7.78 | 5.82 | 9.04 | 5.43 | 5.52 | 5.5 | 5.21 | 4.6 | 4.6 | 4.52 | 4.25 | 5.37
BLD8PST |  |  | VAV_POD_2_FAN | 6.13 | 5.04 | 4.77 | 5.01 | 5.96 | 4.37 | 7.14 | 4.18 | 4.14 | 4.17 | 3.96 | 3.43 | 3.47 | 3.57 | 3.34 | 4.21
BLD8PST |  |  | VAV_POD_3_FAN | 6.39 | 5.19 | 5.03 | 5.11 | 6.3 | 4.62 | 7.36 | 4.33 | 4.38 | 4.46 | 4.14 | 3.65 | 3.65 | 3.57 | 3.35 | 4.23
BLD8PST |  | Utility Costs
BLD8PST |  |  | Electric Utility Rates
BLD8PST |  |  | Average Annual Rate ($/kWh) | 0.089984 | 0.12021 | 0.091203 | 0.09775 | 0.13039 | 0.10004 | 0.14664 | 0.077139 | 0.037107 | 0.074861 | 0.089644 | 0.037117 | 0.060128 | 0.075748 | 0.058501 | 0.094809
BLD8PST |  |  | Total Cost ($/m2) | 18.85 | 22.13 | 17.17 | 16.12 | 20.94 | 17.43 | 21.62 | 12.1 | 5.8 | 10.72 | 13.64 | 5.5 | 8.94 | 10.95 | 8.34 | 13.53
BLD8PST |  |  | Gas Utility Rates
BLD8PST |  |  | Average Annual Rate ($/MJ) | 0.01144 | 0.0081102 | 0.0083814 | 0.0098851 | 0.008493 | 0.0078445 | 0.0085253 | 0.0097537 | 0.0069626 | 0.0083909 | 0.0083971 | 0.0069694 | 0.0078978 | 0.0081789 | 0.0078834 | 0.0041217
BLD8PST |  |  | Total Cost ($/m2) | 0.67 | 1.02 | 0.83 | 1.97 | 0.9 | 1.01 | 1.55 | 2.64 | 1.46 | 2.13 | 3.09 | 1.87 | 3.63 | 3.12 | 4.31 | 4.23
BLD8PST |  |  | Total Utility Costs
BLD8PST |  |  | Cost Intensity ($/m2) | 19.51 | 23.15 | 18 | 18.09 | 21.84 | 18.44 | 23.18 | 14.74 | 7.25 | 12.85 | 16.73 | 7.37 | 12.57 | 14.07 | 12.66 | 17.76
BLD8PST |  | Energy - End Uses
BLD8PST |  |  | Electricity (kWh)
BLD8PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Cooling | 447433.3333 | 289308.3333 | 308127.7778 | 164836.1111 | 133258.3333 | 219402.7778 | 50558.3333 | 116205.5556 | 102127.7778 | 29919.4444 | 84388.8889 | 58672.2222 | 63283.3333 | 35013.8889 | 25650 | 15430.5556
BLD8PST |  |  | Interior Lighting | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556
BLD8PST |  |  | Exterior Lighting | 45977.7778 | 45961.1111 | 45952.7778 | 45944.4444 | 45911.1111 | 45900 | 45925 | 45897.2222 | 45913.8889 | 45822.2222 | 45902.7778 | 45877.7778 | 45872.2222 | 45863.8889 | 45836.1111 | 45555.5556
BLD8PST |  |  | Interior Equipment | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556
BLD8PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans | 68077.7778 | 52705.5556 | 62483.3333 | 46188.8889 | 48675 | 55277.7778 | 41552.7778 | 39947.2222 | 49616.6667 | 33586.1111 | 40247.2222 | 38786.1111 | 37244.4444 | 37661.1111 | 33563.8889 | 43516.6667
BLD8PST |  |  | Pumps | 13.8889 | 152.7778 | 94.4444 | 297.2222 | 83.3333 | 158.3333 | 197.2222 | 416.6667 | 316.6667 | 325 | 597.2222 | 461.1111 | 913.8889 | 719.4444 | 1163.8889 | 2975
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Refrigeration | 21819.4444 | 20827.7778 | 20855.5556 | 19883.3333 | 19886.1111 | 20172.2222 | 19016.6667 | 19263.8889 | 19252.7778 | 18625 | 18827.7778 | 18716.6667 | 18616.6667 | 18261.1111 | 17955.5556 | 17416.6667
BLD8PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 1439183.3333 | 1264819.4444 | 1293372.2222 | 1133011.1111 | 1103675 | 1196775 | 1013111.1111 | 1077588.8889 | 1073091.6667 | 984141.6667 | 1045825 | 1018375 | 1021794.4444 | 993377.7778 | 980030.5556 | 980755.5556
BLD8PST |  |  | Gas (MJ)
BLD8PST |  |  | Heating | 55340 | 498350 | 321010 | 978500 | 341960 | 514200 | 849310 | 1449300 | 1034130 | 1329100 | 2104560 | 1420170 | 2719130 | 2185470 | 3302910 | 6573400
BLD8PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Equipment | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340
BLD8PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 110950 | 134930 | 123070 | 156810 | 150460 | 139040 | 169040 | 174170 | 170860 | 181250 | 189090 | 187900 | 202260 | 203840 | 222570 | 246820
BLD8PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 400630 | 867620 | 678410 | 1369650 | 726750 | 887580 | 1252690 | 1857810 | 1439330 | 1744690 | 2527990 | 1842420 | 3155730 | 2623640 | 3759820 | 7054560
BLD8PST |  |  | Purchased Cooling (MJ)
BLD8PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Purchased Heating (MJ)
BLD8PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total Building (MJ) | 5581690 | 5420970 | 5334550 | 5448490 | 4699980 | 5195970 | 4899890 | 5737130 | 5302460 | 5287600 | 6292960 | 5508560 | 6834190 | 6199810 | 7287930 | 10585280
BLD8PST |  | Energy - End Use Intensities
BLD8PST |  |  | Electricity (MJ/m2)
BLD8PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Cooling (elec) | 234.4288 | 151.5806 | 161.4408 | 86.3644 | 69.8195 | 114.9542 | 26.4896 | 60.8849 | 53.509 | 15.676 | 44.2148 | 30.7408 | 33.1567 | 18.3452 | 13.4391 | 8.0847
BLD8PST |  |  | Interior Lighting (elec) | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742
BLD8PST |  |  | Exterior Lighting (elec) | 24.0897 | 24.0809 | 24.0766 | 24.0722 | 24.0547 | 24.0489 | 24.062 | 24.0474 | 24.0562 | 24.0082 | 24.0504 | 24.0373 | 24.0343 | 24.03 | 24.0154 | 23.8684
BLD8PST |  |  | Interior Equipment (elec) | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467
BLD8PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans (elec) | 35.6688 | 27.6146 | 32.7376 | 24.2003 | 25.5028 | 28.9623 | 21.7712 | 20.93 | 25.9962 | 17.5971 | 21.0872 | 20.3216 | 19.5139 | 19.7322 | 17.5855 | 22.8002
BLD8PST |  |  | Pumps (elec) | 0.007277 | 0.080047 | 0.049483 | 0.15573 | 0.043662 | 0.082957 | 0.10333 | 0.21831 | 0.16591 | 0.17028 | 0.31291 | 0.2416 | 0.47882 | 0.37695 | 0.60981 | 1.5587
BLD8PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Refrigeration (elec) | 11.4321 | 10.9125 | 10.9271 | 10.4177 | 10.4192 | 10.5691 | 9.9636 | 10.0931 | 10.0873 | 9.7584 | 9.8646 | 9.8064 | 9.754 | 9.5677 | 9.4077 | 9.1253
BLD8PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 754.0474 | 662.691 | 677.651 | 593.6312 | 578.2608 | 627.0397 | 530.8107 | 564.5932 | 562.2369 | 515.6324 | 547.9508 | 533.5686 | 535.3602 | 520.4715 | 513.4784 | 513.8582
BLD8PST |  |  | Gas (MJ/m2)
BLD8PST |  |  | Heating (gas) | 8.0541 | 72.5295 | 46.7195 | 142.4101 | 49.7686 | 74.8363 | 123.6079 | 210.93 | 150.5065 | 193.4362 | 306.296 | 206.6904 | 395.7401 | 318.0716 | 480.703 | 956.6875
BLD8PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Equipment (gas) | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057
BLD8PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems (gas) | 16.1476 | 19.6376 | 17.9115 | 22.822 | 21.8978 | 20.2358 | 24.602 | 25.3486 | 24.8668 | 26.379 | 27.52 | 27.3468 | 29.4368 | 29.6667 | 32.3927 | 35.922
BLD8PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 58.3074 | 126.2727 | 98.7353 | 199.3378 | 105.7706 | 129.1777 | 182.3155 | 270.3842 | 209.479 | 253.9208 | 367.9217 | 268.1444 | 459.2825 | 381.8425 | 547.2013 | 1026.7152
BLD8PST |  |  | Purchased Cooling (MJ/m2)
BLD8PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Purchased Heating (MJ/m2)
BLD8PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Total Building (MJ/m2) | 812.3548 | 788.9638 | 776.3863 | 792.969 | 684.0314 | 756.2174 | 713.1262 | 834.9774 | 771.7159 | 769.5532 | 915.8725 | 801.7115 | 994.6427 | 902.3155 | 1060.6797 | 1540.5734
BLD8PST |  | Peak Energy Demand
BLD8PST |  |  | Electricity Peak Demand (kW)
BLD8PST |  |  | Jan | 381.2075 | 332.7042 | 286.7629 | 249.6318 | 341.182 | 245.8522 | 225.4408 | 224.0862 | 228.5988 | 214.0699 | 214.9341 | 233.8153 | 214.8986 | 217.6628 | 214.2514 | 225.1914
BLD8PST |  |  | Feb | 395.2114 | 327.1771 | 311.9248 | 245.2843 | 324.9817 | 259.0663 | 268.5807 | 218.3645 | 261.0752 | 226 | 214.0195 | 221.8527 | 211.1988 | 228.8232 | 211.6779 | 219.6623
BLD8PST |  |  | Mar | 400.6059 | 329.0563 | 368.3571 | 288.2226 | 324.8376 | 287.5971 | 246.4736 | 276.0518 | 266.9076 | 252.9001 | 250.4733 | 262.8294 | 224.1682 | 249.1305 | 210.4526 | 219.5429
BLD8PST |  |  | Apr | 426.6091 | 365.3151 | 381.1939 | 324.0473 | 332.7418 | 363.3905 | 282.2946 | 276.4319 | 312.0278 | 237.2476 | 254.7511 | 278.9215 | 245.5243 | 238.6806 | 228.4284 | 212.8111
BLD8PST |  |  | May | 468.0774 | 433.1108 | 429.7863 | 381.8223 | 338.6262 | 409.85 | 289.8218 | 339.3574 | 345.332 | 283.6273 | 323.5412 | 305.8527 | 332.8639 | 278.4592 | 263.555 | 258.1199
BLD8PST |  |  | Jun | 480.0925 | 438.5544 | 502.6763 | 419.8194 | 339.3261 | 461.0074 | 295.8412 | 407.8495 | 370.7277 | 298.5799 | 394.8909 | 348.8457 | 370.2918 | 336.5368 | 324.5345 | 299.6878
BLD8PST |  |  | Jul | 326.834 | 329.585 | 383.3296 | 330.2987 | 217.9179 | 357.0461 | 199.1601 | 316.1542 | 283.4519 | 204.1374 | 280.6999 | 251.5596 | 257.0465 | 236.9615 | 219.1866 | 168.9102
BLD8PST |  |  | Aug | 354.1305 | 325.3832 | 388.0655 | 290.7178 | 251.2005 | 337.9571 | 191.7032 | 312.4936 | 263.9386 | 189.7307 | 287.4116 | 250.8309 | 253.1199 | 209.0136 | 199.8074 | 170.7735
BLD8PST |  |  | Sep | 465.94 | 436.5751 | 451.3906 | 402.6543 | 390.8434 | 410.83 | 387.5142 | 370.0072 | 337.0429 | 320.0289 | 352.3631 | 327.3552 | 324.3787 | 293.76 | 298.7013 | 222.9598
BLD8PST |  |  | Oct | 454.2639 | 390.5671 | 383.9025 | 342.9507 | 372.3097 | 368.0199 | 289.9125 | 323.7683 | 311.9166 | 261.9547 | 294.0209 | 307.7709 | 257.5871 | 265.1669 | 234.7414 | 217.4341
BLD8PST |  |  | Nov | 412.7457 | 350.1583 | 345.4922 | 270.5823 | 339.9566 | 270.7928 | 241.4846 | 292.1742 | 252.38 | 223.8976 | 286.7967 | 250.6001 | 236.9345 | 217.695 | 213.3856 | 221.0432
BLD8PST |  |  | Dec | 370.5446 | 331.5526 | 277.5235 | 244.3594 | 349.9036 | 263.2183 | 228.9843 | 214.2596 | 223.2132 | 214.0836 | 214.1163 | 217.0407 | 213.7387 | 217.1825 | 213.5352 | 225.1252
BLD8PST |  |  | Time of Peak Electrical Demand
BLD8PST |  |  | Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:00 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 27-JAN-16:00 | 27-JAN-16:00 | 24-JAN-12:00 | 04-JAN-16:00 | 05-JAN-08:09 | 09-JAN-16:40 | 02-JAN-11:09
BLD8PST |  |  | Feb | 23-FEB-12:30 | 23-FEB-14:00 | 28-FEB-15:00 | 27-FEB-15:00 | 13-FEB-11:00 | 08-FEB-14:00 | 14-FEB-12:00 | 15-FEB-12:00 | 14-FEB-15:00 | 21-FEB-13:00 | 01-FEB-16:00 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 02-FEB-09:39
BLD8PST |  |  | Mar | 13-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-13:00 | 31-MAR-14:50 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 01-MAR-11:20 | 14-MAR-07:10
BLD8PST |  |  | Apr | 03-APR-13:00 | 21-APR-14:00 | 26-APR-14:00 | 14-APR-14:00 | 13-APR-11:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-14:00 | 21-APR-14:00 | 14-APR-13:00 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 24-APR-11:00
BLD8PST |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-11:30 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-14:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
BLD8PST |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-13:50 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-13:00 | 20-JUN-13:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-11:00 | 30-JUN-11:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-14:00
BLD8PST |  |  | Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-15:00 | 24-JUL-13:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 17-JUL-15:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD8PST |  |  | Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-13:00
BLD8PST |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-11:00 | 20-SEP-15:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-15:00 | 13-SEP-14:00 | 06-SEP-11:00 | 06-SEP-14:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-14:00
BLD8PST |  |  | Oct | 06-OCT-13:00 | 13-OCT-14:00 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 30-OCT-13:50 | 03-OCT-11:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 27-OCT-11:00 | 30-OCT-07:10
BLD8PST |  |  | Nov | 01-NOV-11:00 | 27-NOV-12:00 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-11:00 | 02-NOV-14:30 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 24-NOV-16:00 | 30-NOV-10:20
BLD8PST |  |  | Dec | 19-DEC-12:00 | 19-DEC-14:00 | 11-DEC-15:39 | 01-DEC-14:00 | 19-DEC-12:00 | 05-DEC-14:50 | 07-DEC-14:00 | 20-DEC-16:00 | 08-DEC-14:00 | 28-DEC-16:19 | 12-DEC-16:19 | 21-DEC-14:00 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 28-DEC-11:20
BLD8PST |  | Source Energy
BLD8PST |  |  | Total Source Energy (GJ) | 17623.07 | 17485.2 | 15468.2 | 15216.87 | 13090.76 | 16380.33 | 12656.02 | 15901.18 | 14389.61 | 8076.95 | 16111.15 | 14176.19 | 16088.93 | 15295.76 | 16231.83 | 20315.3
BLD8PST |  |  | Total Source Energy (MJ/m2) | 2564.85 | 2544.78 | 2251.23 | 2214.65 | 1905.22 | 2383.98 | 1841.95 | 2314.25 | 2094.25 | 1175.51 | 2344.8 | 2063.19 | 2341.57 | 2226.13 | 2362.37 | 2956.67
BLD8PST |  | Water Consumption (m3)
BLD8PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Water Systems | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
BLD8PST |  |  | Total Building | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
BLD8PST |  | Emissions
BLD8PST |  |  | Carbon Equivalent (kg) | 401920.2395 | 437539.6637 | 402671.0235 | 373707.2888 | 142087.1502 | 419647.3816 | 140987.4193 | 324294.6683 | 464310.6379 | 103140.5189 | 603167.1279 | 449227.4819 | 406659.4963 | 410329.1862 | 403257.2521 | 403184.7816
BLD8PST |  |  | CO2 (kg) | 934812.1371 | 1103860 | 953536.2938 | 863469.087 | 382223.5529 | 1002270 | 381367.8941 | 748905.7713 | 1096400 | 261170.4918 | 1418200 | 1065320 | 970732.1227 | 981023.9254 | 969248.1457 | 1058860
BLD8PST |  |  | NOX (kg) | 1630.7782 | 1432.5414 | 1583.9806 | 1594.3487 | 329.0698 | 1609.804 | 329.765 | 1391.7142 | 1860.1855 | 356.1071 | 2462.1372 | 1787.8715 | 1620.6503 | 1622.8683 | 1589.0832 | 1199.7655
BLD8PST |  |  | SO2 (kg) | 6160.3906 | 6033.4174 | 5201.0909 | 3977.234 | 3211.7545 | 6583.4503 | 2948.3665 | 3934.1294 | 4686.3604 | 761.1296 | 7048.6976 | 4447.5293 | 2412.4444 | 2653.1433 | 2314.0361 | 4994.3237
BLD8PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8PST |  |  | Hg (kg) | 0.0281 | 0.017 | 0.0142 | 0.0147 | 0.0015 | 0.0124 | 0.0015 | 0.016 | 0.0184 | 0.0031 | 0.0215 | 0.0175 | 0.0179 | 0.0187 | 0.0173 | 0.0177
BLD8PST |  |  | Water for Electricity (m3) | 762.4192 | 2058.01 | 38418.8 | 7074.06 | 19378 | 32832.3 | 17788 | 244.6533 | 4872.69 | 10054.8 | 1622.53 | 4624.23 | 1585.25 | 62924.7 | 1520.46 | 1002.02
BLD8NEW |  | Program
BLD8NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD8NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD8NEW |  |  | Weighting Factor | 11.3935 | 166.9938 | 29.394 | 168.9694 |  | 79.8242 | 8.5151 | 160.1074 | 5.3818 | 16.7523 | 164.6314 | 40.0073 | 30.0711 | 6.7034 | 4.1682 | 0.59086
BLD8NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD8NEW |  |  | Exterior walls
BLD8NEW | TypeWall |  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
BLD8NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BLD8NEW |  |  | Roof
BLD8NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD8NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD8NEW |  |  | Window
BLD8NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD8NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD8NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD8NEW |  |  | Skylights/TDD
BLD8NEW |  |  | U-Factor (W / m2·K) | 5.765 | 5.765 | 5.765 | 2.627 | 2.627 | 2.627 | 5.679 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.561
BLD8NEW |  |  | SHGC | 0.174 | 0.174 | 0.174 | 0.229 | 0.229 | 0.229 | 0.394 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.777 | 0.767
BLD8NEW |  |  | Visible transmittance | 0.029 | 0.029 | 0.029 | 0.008 | 0.008 | 0.008 | 0.09 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.855 | 0.855
BLD8NEW |  |  | Foundation
BLD8NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD8NEW |  |  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
BLD8NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD8NEW |  | HVAC
BLD8NEW |  |  | HVAC Sizing
BLD8NEW | HVAC |  | Air Conditioning (kW) | 575.968 | 590.1967 | 592.1855 | 550.0136 | 436.4604 | 501.0436 | 535.5038 | 559.0367 | 410.6226 | 379.3659 | 529.5895 | 384.29 | 515.2505 | 336.3166 | 475.6128 | 288.3576
BLD8NEW |  |  | PSZ-AC_1:6_COOLC DXCOIL | 16.3647 | 16.2714 | 15.6012 | 15.8582 | 14.053 | 14.6127 | 18.3985 | 15.7188 | 14.4702 | 11.1346 | 15.3143 | 13.6958 | 14.9693 | 10.8655 | 13.3607 | 6.7025
BLD8NEW |  |  | PSZ-AC_2:5_COOLC DXCOIL | 28.7023 | 29.2238 | 28.4251 | 29.0374 | 26.6221 | 26.6221 | 24.7137 | 29.5453 | 27.0627 | 23.9674 | 28.4091 | 26.0082 | 27.7026 | 21.2689 | 29.3286 | 17.7466
BLD8NEW |  |  | PSZ-AC_2:7_COOLC DXCOIL | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 43.4953 | 56.2748 | 52.9305 | 50.5807 | 56.2748 | 53.3823 | 56.2748 | 46.2592 | 56.2748 | 37.5134
BLD8NEW |  |  | VAV_OTHER_COOLC DXCOIL | 137.6748 | 141.0787 | 135.8737 | 130.6096 | 92.4946 | 107.3017 | 106.934 | 129.9149 | 85.2799 | 74.5035 | 121.2614 | 78.177 | 116.6401 | 75.0473 | 102.6877 | 74.9051
BLD8NEW |  |  | VAV_POD_1_COOLC DXCOIL | 131.6648 | 135.873 | 139.6824 | 123.7432 | 95.2309 | 114.6447 | 132.3678 | 128.5653 | 90.0117 | 85.0729 | 121.1304 | 83.0797 | 117.7423 | 72.0018 | 107.9826 | 58.0111
BLD8NEW |  |  | VAV_POD_2_COOLC DXCOIL | 101.0282 | 103.7672 | 105.6192 | 95.9135 | 75.555 | 90.311 | 102.5954 | 96.9786 | 69.403 | 65.4337 | 91.1722 | 63.9685 | 88.4583 | 53.7708 | 79.6963 | 46.9812
BLD8NEW |  |  | VAV_POD_3_COOLC DXCOIL | 104.2584 | 107.7078 | 110.7092 | 98.5768 | 76.2299 | 91.2765 | 106.9993 | 102.039 | 71.4647 | 68.6731 | 96.0272 | 65.9784 | 93.463 | 57.1033 | 86.282 | 46.4977
BLD8NEW | HEAT |  | Heating (kW) | 451.4675 | 582.725 | 501.3631 | 586.7039 | 397.948 | 478.1787 | 646.2082 | 655.4372 | 510.1186 | 511.352 | 722.8907 | 560.197 | 761.0452 | 662.5286 | 738.6563 | 821.8783
BLD8NEW |  |  | HEATSYS1 BOILER | 294.7839 | 376.2157 | 328.7171 | 365.2853 | 240.7417 | 295.1329 | 449.6794 | 409.0096 | 313.9581 | 307.4954 | 437.707 | 330.4491 | 454.6996 | 388.1508 | 428.839 | 454.2423
BLD8NEW |  |  | PSZ-AC_1:6_HEATC | 25.5141 | 33.49 | 27.0916 | 35.2097 | 22.7872 | 27.4311 | 42.0146 | 38.85 | 30.6105 | 26.6694 | 44.2171 | 34.2736 | 46.7092 | 38.6706 | 42.6726 | 39.7672
BLD8NEW |  |  | PSZ-AC_2:5_HEATC | 43.4319 | 57.1937 | 47.8329 | 61.2629 | 43.1683 | 49.9752 | 53.6519 | 68.4903 | 55.0376 | 56.9032 | 78.484 | 63.5542 | 84.0404 | 75.6966 | 87.4088 | 105.2941
BLD8NEW |  |  | PSZ-AC_2:7_HEATC | 87.7376 | 115.8256 | 97.7215 | 124.946 | 91.2508 | 105.6395 | 100.8623 | 139.0873 | 110.5125 | 120.2841 | 162.4826 | 131.9201 | 175.596 | 160.0105 | 179.7358 | 222.5747
BLD8NEW |  |  | HVAC Efficiency
BLD8NEW | COP |  | Air Conditioning (COP) | 3.2628 | 3.2622 | 3.2612 | 3.2641 | 3.2697 | 3.265 | 3.2633 | 3.2637 | 3.2842 | 3.2941 | 3.2646 | 3.2973 | 3.2649 | 3.294 | 3.2673 | 3.3392
BLD8NEW |  |  | PSZ-AC_1:6_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD8NEW |  |  | PSZ-AC_2:5_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67
BLD8NEW |  |  | PSZ-AC_2:7_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.5
BLD8NEW |  |  | VAV_OTHER_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD8NEW |  |  | VAV_POD_1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3
BLD8NEW |  |  | VAV_POD_2_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
BLD8NEW |  |  | VAV_POD_3_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
BLD8NEW | EffHeat |  | Heating Efficiency (%) | 0.76347 | 0.76374 | 0.76332 | 0.76461 | 0.76517 | 0.76472 | 0.76208 | 0.76246 | 0.76489 | 0.76523 | 0.76306 | 0.7658 | 0.7633 | 0.76359 | 0.76374 | 0.76439
BLD8NEW |  |  | HEATSYS1 BOILER | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
BLD8NEW |  |  | PSZ-AC_1:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD8NEW |  |  | PSZ-AC_2:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
BLD8NEW |  |  | PSZ-AC_2:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD8NEW |  |  | HVAC Control - Economizer
BLD8NEW |  |  | PSZ-AC_1:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD8NEW |  |  | PSZ-AC_2:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD8NEW |  |  | PSZ-AC_2:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
BLD8NEW |  |  | VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8NEW |  |  | VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8NEW |  |  | VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8NEW |  |  | VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD8NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 25.04 | 25.62 | 25.69 | 23.99 | 20.92 | 22.63 | 32.59 | 24.36 | 23.6 | 21.28 | 23.17 | 21.63 | 22.59 | 21.27 | 21.21 | 19.26
BLD8NEW |  |  | BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
BLD8NEW |  |  | CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD8NEW |  |  | KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
BLD8NEW |  |  | PSZ-AC_1:6_FAN | 0.66 | 0.66 | 0.63 | 0.64 | 0.57 | 0.59 | 0.94 | 0.63 | 0.63 | 0.5 | 0.62 | 0.59 | 0.6 | 0.55 | 0.54 | 0.4
BLD8NEW |  |  | PSZ-AC_2:5_FAN | 1.16 | 1.18 | 1.14 | 1.17 | 1.07 | 1.07 | 1.33 | 1.19 | 1.22 | 1.07 | 1.14 | 1.13 | 1.12 | 1.07 | 1.18 | 1.07
BLD8NEW |  |  | PSZ-AC_2:7_FAN | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
BLD8NEW |  |  | VAV_OTHER_FAN | 5.54 | 5.68 | 5.47 | 5.26 | 4.32 | 4.63 | 6.21 | 5.23 | 4.9 | 3.99 | 4.88 | 4.36 | 4.7 | 4.53 | 4.27 | 4.53
BLD8NEW |  |  | VAV_POD_1_FAN | 5.3 | 5.47 | 5.63 | 4.98 | 4.23 | 4.79 | 7.78 | 5.18 | 5.03 | 4.56 | 4.88 | 4.52 | 4.74 | 4.35 | 4.4 | 3.5
BLD8NEW |  |  | VAV_POD_2_FAN | 4.07 | 4.18 | 4.25 | 3.86 | 3.24 | 3.64 | 5.93 | 3.91 | 3.73 | 3.38 | 3.67 | 3.34 | 3.56 | 3.21 | 3.21 | 2.84
BLD8NEW |  |  | VAV_POD_3_FAN | 4.2 | 4.34 | 4.46 | 3.97 | 3.38 | 3.8 | 6.29 | 4.11 | 3.98 | 3.67 | 3.87 | 3.58 | 3.76 | 3.45 | 3.5 | 2.81
BLD8NEW |  | Utility Costs
BLD8NEW |  |  | Electric Utility Rates
BLD8NEW |  |  | Average Annual Rate ($/kWh) | 0.089546 | 0.12149 | 0.095129 | 0.09813 | 0.12865 | 0.10058 | 0.14698 | 0.078315 | 0.037147 | 0.074931 | 0.088864 | 0.037159 | 0.061318 | 0.076246 | 0.05962 | 0.094216
BLD8NEW |  |  | Total Cost ($/m2) | 14.92 | 18.39 | 14.75 | 13.08 | 15.97 | 14.23 | 17.56 | 10.11 | 4.74 | 8.65 | 11.06 | 4.5 | 7.5 | 8.93 | 6.93 | 10.71
BLD8NEW |  |  | Gas Utility Rates
BLD8NEW |  |  | Average Annual Rate ($/MJ) | 0.011447 | 0.0081205 | 0.0084031 | 0.01001 | 0.008472 | 0.0078898 | 0.0085206 | 0.0097678 | 0.0069858 | 0.0083834 | 0.0084278 | 0.006983 | 0.0078983 | 0.0082014 | 0.0078866 | 0.0041238
BLD8NEW |  |  | Total Cost ($/m2) | 0.61 | 0.86 | 0.75 | 1.51 | 0.66 | 0.85 | 1.34 | 2.33 | 1.22 | 1.73 | 2.56 | 1.63 | 3.26 | 2.75 | 3.83 | 3.08
BLD8NEW |  |  | Total Utility Costs
BLD8NEW |  |  | Cost Intensity ($/m2) | 15.53 | 19.25 | 15.5 | 14.59 | 16.63 | 15.08 | 18.91 | 12.44 | 5.96 | 10.39 | 13.62 | 6.13 | 10.76 | 11.69 | 10.76 | 13.78
BLD8NEW |  | Energy - End Uses
BLD8NEW |  |  | Electricity (kWh)
BLD8NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Cooling | 343791.6667 | 250313.8889 | 268550 | 134194.4444 | 78413.8889 | 183755.5556 | 42627.7778 | 107827.7778 | 91358.3333 | 24666.6667 | 78058.3333 | 55794.4444 | 62525 | 33161.1111 | 25905.5556 | 9783.3333
BLD8NEW |  |  | Interior Lighting | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889
BLD8NEW |  |  | Exterior Lighting | 37480.5556 | 37466.6667 | 37461.1111 | 37455.5556 | 37425 | 37416.6667 | 37436.1111 | 37413.8889 | 37427.7778 | 37352.7778 | 37419.4444 | 37397.2222 | 37394.4444 | 37386.1111 | 37366.6667 | 37136.1111
BLD8NEW |  |  | Interior Equipment | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556
BLD8NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans | 57466.6667 | 47202.7778 | 53850 | 40036.1111 | 32861.1111 | 46666.6667 | 37433.3333 | 37666.6667 | 44327.7778 | 28236.1111 | 36041.6667 | 35597.2222 | 36638.8889 | 31366.6667 | 32286.1111 | 30319.4444
BLD8NEW |  |  | Pumps | 2.7778 | 100 | 66.6667 | 172.2222 | 16.6667 | 97.2222 | 133.3333 | 333.3333 | 230.5556 | 213.8889 | 408.3333 | 361.1111 | 736.1111 | 588.8889 | 933.3333 | 1822.2222
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Refrigeration | 21841.6667 | 20861.1111 | 20911.1111 | 19961.1111 | 19950 | 20269.4444 | 19105.5556 | 19347.2222 | 19363.8889 | 18719.4444 | 18922.2222 | 18819.4444 | 18683.3333 | 18350 | 18027.7778 | 17513.8889
BLD8NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 1144827.7778 | 1040186.1111 | 1065083.3333 | 916061.1111 | 852911.1111 | 972450 | 820980.5556 | 886830.5556 | 876955.5556 | 793430.5556 | 855094.4444 | 832213.8889 | 840225 | 805100 | 798763.8889 | 780819.4444
BLD8NEW |  |  | Gas (MJ)
BLD8NEW |  |  | Heating | 23840 | 363430 | 260030 | 649190 | 157710 | 366910 | 684360 | 1232760 | 800220 | 1009940 | 1666130 | 1188080 | 2407470 | 1872200 | 2886100 | 4651870
BLD8NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Equipment | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340
BLD8NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 108190 | 131580 | 120000 | 152910 | 146710 | 135570 | 164840 | 169830 | 166600 | 176730 | 184390 | 183220 | 197220 | 198760 | 217020 | 240670
BLD8NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 366380 | 729350 | 614370 | 1036440 | 538760 | 736820 | 1083550 | 1636930 | 1201160 | 1421010 | 2084860 | 1605650 | 2839030 | 2305310 | 3337470 | 5126880
BLD8NEW |  |  | Purchased Cooling (MJ)
BLD8NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Purchased Heating (MJ)
BLD8NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total Building (MJ) | 4487750 | 4474010 | 4448670 | 4334260 | 3609240 | 4237640 | 4039080 | 4829530 | 4358200 | 4277370 | 5163200 | 4601620 | 5863840 | 5203660 | 6213010 | 7937830
BLD8NEW |  | Energy - End Use Intensities
BLD8NEW |  |  | Electricity (MJ/m2)
BLD8NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Cooling (elec) | 180.1266 | 131.1498 | 140.7044 | 70.31 | 41.0843 | 96.2771 | 22.3344 | 56.4954 | 47.8664 | 12.9239 | 40.898 | 29.233 | 32.7594 | 17.3745 | 13.573 | 5.1259
BLD8NEW |  |  | Interior Lighting (elec) | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571
BLD8NEW |  |  | Exterior Lighting (elec) | 19.6376 | 19.6303 | 19.6274 | 19.6245 | 19.6085 | 19.6041 | 19.6143 | 19.6027 | 19.61 | 19.5707 | 19.6056 | 19.5939 | 19.5925 | 19.5881 | 19.5779 | 19.4571
BLD8NEW |  |  | Interior Equipment (elec) | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467
BLD8NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans (elec) | 30.1092 | 24.7315 | 28.2142 | 20.9766 | 17.2173 | 24.4506 | 19.6129 | 19.7351 | 23.2251 | 14.7941 | 18.8837 | 18.6509 | 19.1966 | 16.4343 | 16.916 | 15.8856
BLD8NEW |  |  | Pumps (elec) | 0.0014554 | 0.052394 | 0.034929 | 0.090234 | 0.0087324 | 0.050939 | 0.069859 | 0.17465 | 0.1208 | 0.11207 | 0.21394 | 0.1892 | 0.38568 | 0.30854 | 0.48901 | 0.95474
BLD8NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Refrigeration (elec) | 11.4437 | 10.93 | 10.9562 | 10.4584 | 10.4526 | 10.62 | 10.0102 | 10.1368 | 10.1455 | 9.8079 | 9.9141 | 9.8603 | 9.789 | 9.6143 | 9.4455 | 9.1762
BLD8NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 599.8224 | 544.9964 | 558.041 | 479.9622 | 446.8753 | 509.5066 | 430.1455 | 464.6471 | 459.4731 | 415.711 | 448.0192 | 436.0311 | 440.2285 | 421.8251 | 418.5053 | 409.1035
BLD8NEW |  |  | Gas (MJ/m2)
BLD8NEW |  |  | Heating (gas) | 3.4697 | 52.8933 | 37.8446 | 94.4826 | 22.953 | 53.3998 | 99.6012 | 179.4149 | 116.4634 | 146.9859 | 242.4873 | 172.9122 | 350.3813 | 272.4785 | 420.0408 | 677.0295
BLD8NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Equipment (gas) | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057
BLD8NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems (gas) | 15.7459 | 19.1501 | 17.4647 | 22.2544 | 21.3521 | 19.7308 | 23.9907 | 24.7169 | 24.2468 | 25.7211 | 26.836 | 26.6657 | 28.7032 | 28.9274 | 31.5849 | 35.0269
BLD8NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 53.3227 | 106.149 | 89.4149 | 150.8427 | 78.4107 | 107.2362 | 157.699 | 238.2375 | 174.8159 | 206.8127 | 303.4289 | 233.6851 | 413.1902 | 335.513 | 485.7328 | 746.1621
BLD8NEW |  |  | Purchased Cooling (MJ/m2)
BLD8NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Purchased Heating (MJ/m2)
BLD8NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Total Building (MJ/m2) | 653.1436 | 651.1439 | 647.456 | 630.8048 | 525.286 | 616.7428 | 587.8446 | 702.886 | 634.289 | 622.5251 | 751.4481 | 669.7162 | 853.4187 | 757.3366 | 904.2366 | 1155.2656
BLD8NEW |  | Peak Energy Demand
BLD8NEW |  |  | Electricity Peak Demand (kW)
BLD8NEW |  |  | Jan | 308.6216 | 276.7666 | 237.1244 | 199.9079 | 248.4953 | 200.1397 | 182.1581 | 182.1265 | 186.0519 | 170.9784 | 172.403 | 188.5916 | 172.8417 | 174.6318 | 171.9955 | 179.8422
BLD8NEW |  |  | Feb | 318.7029 | 268.9776 | 261.2852 | 194.6986 | 235.7891 | 212.2588 | 219.7866 | 177.7454 | 214.8451 | 182.1433 | 171.6209 | 180.6041 | 171.1956 | 182.9465 | 171.4609 | 174.3006
BLD8NEW |  |  | Mar | 321.1568 | 273.3169 | 311.2059 | 230.3395 | 235.0965 | 238.5135 | 199.9095 | 229.2015 | 220.27 | 204.0169 | 204.5449 | 221.1896 | 182.7244 | 203.7206 | 170.2119 | 174.1529
BLD8NEW |  |  | Apr | 332.902 | 306.019 | 326.6886 | 263.2661 | 250.2967 | 303.5029 | 227.0539 | 229.3392 | 261.8968 | 191.3354 | 210.7063 | 238.0671 | 205.903 | 193.1573 | 187.1055 | 169.2234
BLD8NEW |  |  | May | 353.214 | 360.1531 | 370.266 | 312.3118 | 249.0207 | 343.1925 | 232.3958 | 290.7665 | 293.4462 | 227.7693 | 275.5566 | 264.7027 | 287.9175 | 231.9541 | 224.5852 | 193.8257
BLD8NEW |  |  | Jun | 361.9644 | 362.7388 | 436.0828 | 336.9152 | 246.5343 | 391.2356 | 235.463 | 357.2738 | 316.9159 | 240.8478 | 344.2282 | 305.8233 | 331.1498 | 283.7687 | 284.2948 | 224.4841
BLD8NEW |  |  | Jul | 266.0854 | 289.3521 | 338.5652 | 279.4674 | 153.3377 | 307.645 | 163.2471 | 284.7045 | 250.028 | 166.9061 | 249.975 | 228.2547 | 229.9579 | 206.9396 | 205.9703 | 127.2829
BLD8NEW |  |  | Aug | 282.4925 | 287.4309 | 344.1463 | 242.8186 | 180.5667 | 291.005 | 159.208 | 282.9068 | 228.7069 | 153.6812 | 257.7546 | 223.8792 | 233.7093 | 181.3073 | 185.7651 | 124.2931
BLD8NEW |  |  | Sep | 357.1485 | 364.2892 | 386.0629 | 326.8299 | 280.4494 | 343.5695 | 322.1369 | 321.0934 | 283.7168 | 258.6011 | 301.677 | 285.6783 | 287.2306 | 243.5188 | 259.5245 | 172.5394
BLD8NEW |  |  | Oct | 349.3727 | 331.5977 | 325.2432 | 277.8686 | 274.6009 | 306.8462 | 236.9031 | 272.8967 | 261.918 | 211.9369 | 240.7056 | 266.7137 | 217.4079 | 218.4448 | 193.0417 | 172.8921
BLD8NEW |  |  | Nov | 332.9678 | 295.18 | 289.8613 | 218.853 | 244.4476 | 220.8909 | 196.2269 | 245.35 | 207.2287 | 180.5557 | 234.5677 | 207.0611 | 196.5779 | 174.4751 | 171.232 | 176.6155
BLD8NEW |  |  | Dec | 297.9262 | 275.02 | 226.6029 | 195.9179 | 252.2025 | 214.5031 | 185.1271 | 171.9232 | 181.3472 | 170.987 | 171.735 | 175.6752 | 171.8336 | 174.4043 | 171.3805 | 179.7573
BLD8NEW |  |  | Time of Peak Electrical Demand
BLD8NEW |  |  | Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:00 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 27-JAN-16:00 | 27-JAN-16:00 | 24-JAN-12:00 | 04-JAN-16:00 | 05-JAN-08:09 | 09-JAN-16:49 | 02-JAN-11:09
BLD8NEW |  |  | Feb | 23-FEB-12:30 | 23-FEB-14:00 | 28-FEB-15:00 | 27-FEB-15:00 | 13-FEB-11:00 | 08-FEB-14:00 | 14-FEB-12:00 | 15-FEB-12:00 | 14-FEB-15:00 | 21-FEB-13:00 | 01-FEB-16:00 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-09:39
BLD8NEW |  |  | Mar | 13-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 30-MAR-11:00 | 31-MAR-14:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 01-MAR-11:20 | 14-MAR-07:10
BLD8NEW |  |  | Apr | 17-APR-12:00 | 21-APR-14:00 | 26-APR-14:00 | 14-APR-14:00 | 11-APR-15:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-14:00 | 21-APR-14:00 | 14-APR-13:00 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 25-APR-10:20
BLD8NEW |  |  | May | 24-MAY-14:00 | 18-MAY-13:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-11:00 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-14:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
BLD8NEW |  |  | Jun | 26-JUN-10:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-13:00 | 20-JUN-13:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-13:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-14:00
BLD8NEW |  |  | Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:50 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD8NEW |  |  | Aug | 21-AUG-13:00 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-14:00 | 04-AUG-15:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-13:00
BLD8NEW |  |  | Sep | 06-SEP-11:00 | 20-SEP-11:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-11:00 | 21-SEP-13:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-15:00 | 13-SEP-14:00 | 06-SEP-11:00 | 06-SEP-14:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-14:00
BLD8NEW |  |  | Oct | 06-OCT-11:00 | 30-OCT-10:50 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 30-OCT-13:30 | 03-OCT-13:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 27-OCT-07:30
BLD8NEW |  |  | Nov | 01-NOV-11:00 | 27-NOV-12:00 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-11:00 | 02-NOV-14:30 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 24-NOV-16:00 | 30-NOV-10:20
BLD8NEW |  |  | Dec | 15-DEC-12:00 | 19-DEC-14:00 | 11-DEC-15:39 | 13-DEC-12:00 | 19-DEC-12:00 | 05-DEC-14:00 | 07-DEC-14:00 | 20-DEC-16:00 | 08-DEC-14:00 | 28-DEC-16:19 | 12-DEC-16:19 | 21-DEC-14:00 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 28-DEC-11:20
BLD8NEW |  | Source Energy
BLD8NEW |  |  | Total Source Energy (GJ) | 14070.69 | 14397.08 | 12798.78 | 12225.66 | 10091.47 | 13327.03 | 10330.61 | 13204.25 | 11786.72 | 6527.51 | 13192.47 | 11694 | 13496.48 | 12592.08 | 13527.76 | 15639.25
BLD8NEW |  |  | Total Source Energy (MJ/m2) | 2047.84 | 2095.34 | 1862.72 | 1779.31 | 1468.71 | 1939.61 | 1503.51 | 1921.74 | 1715.43 | 950.01 | 1920.02 | 1701.94 | 1964.27 | 1832.64 | 1968.82 | 2276.12
BLD8NEW |  | Water Consumption (m3)
BLD8NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Water Systems | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
BLD8NEW |  |  | Total Building | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
BLD8NEW |  | Emissions
BLD8NEW |  |  | Carbon Equivalent (kg) | 320575.1506 | 360117.3871 | 332601.0981 | 300870.3532 | 109391.5854 | 341269.749 | 115483.9662 | 268834.7164 | 379894.5689 | 83413.5829 | 493488.9222 | 368912.0773 | 338798.1899 | 335784.169 | 333594.454 | 312163.9736
BLD8NEW |  |  | CO2 (kg) | 746098.8934 | 908634.3004 | 788132.2246 | 694435.4658 | 294188.2639 | 815219.7825 | 312608.8968 | 621959.3133 | 897301.3229 | 211311.0809 | 1160490 | 875789.1212 | 810951.0542 | 804408.1592 | 804201.6552 | 817493.8013
BLD8NEW |  |  | NOX (kg) | 1299.4896 | 1178.8687 | 1307.0312 | 1285.7066 | 253.2212 | 1308.7992 | 270.4637 | 1150.4578 | 1521.365 | 287.7815 | 2013.9582 | 1465.7784 | 1344.2086 | 1323.7418 | 1308.0805 | 932.0266
BLD8NEW |  |  | SO2 (kg) | 4900.4141 | 4961.8809 | 4283.0753 | 3215.6532 | 2482.016 | 5349.4471 | 2389.248 | 3237.7288 | 3829.81 | 613.6402 | 5763.2153 | 3634.5442 | 1983.8237 | 2150.3281 | 1886.1024 | 3976.0514
BLD8NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD8NEW |  |  | Hg (kg) | 0.0224 | 0.014 | 0.0117 | 0.0118 | 0.0012 | 0.0101 | 0.0012 | 0.0132 | 0.015 | 0.0025 | 0.0176 | 0.0143 | 0.0148 | 0.0152 | 0.0141 | 0.014
BLD8NEW |  |  | Water for Electricity (m3) | 606.4811 | 1692.5 | 31637.6 | 5719.52 | 14975.2 | 26678.2 | 14414.6 | 201.3441 | 3982.08 | 8106.33 | 1326.63 | 3778.92 | 1303.56 | 50998.3 | 1239.23 | 797.7464

## Picture
DOE Commercial Building Benchmark - Primary School

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SchEquip1 | WD | BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69 | 3348.11
| Sat |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
| Sun |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
SchEquip2 | WD | BLDG_EQUIP_SCH |  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 41.25
| Sat |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
| Sun |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69
[5 empty] | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
SchLight1 | WD | BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87 | 3466.2
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchLight2 | WD | BLDG_LIGHT_SCH |  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 40.64
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
|  |  |  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87
[5 empty] | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
SchOcc1 | WD | BLDG_OCC_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75 | 1543.82
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchOcc2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13 | 628.36
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 7.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2176.29
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 22.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25 | 784.83
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  |  |  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82 | 14.1
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  |  |  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
SchGas1 |  | KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 7.2 | 364.18
[5 empty] | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
SchGas2 |  |  |  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.19 | 5.95
[5 empty] | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  |  |  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 7.2
[5 empty] | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Kitchen_Exhaust_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  |  |  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  |  |  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
SetCool1 | WD | CLGSETP_SCH | Temperature | Through 6/30 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296 | 67577.14
[5 empty] | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
| Sat |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
| Sun |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
SetCool2 | WD |  |  | Through 9/1 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
[5 empty] | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
| Sat |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27
| Sun |  |  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 615
|  |  |  | Through 12/31 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
[5 empty] | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
[5 empty] | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
|  | CLGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | SummerDesign | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603 | 0 | 0
[5 empty] | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
SetHeat1 | WD | HTGSETP_SCH | Temperature | Through 6/30 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768 | 40045.71
[5 empty] | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
| Sat |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
| Sun |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
SetHeat1 | WD |  |  | Through 9/1 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
[5 empty] | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
| Sat |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 439
| Sun |  |  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16
|  |  |  | Through 12/31 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
[5 empty] | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
[5 empty] | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
|  | HTGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | WinterDesign | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459 | 0 | 0
[5 empty] | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  | HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
|  | PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
[5 empty] | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
|  | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SchSWH1 | WD | BLDG_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 35.35 | 1646.6
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
| Sun |  |  |  | Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
SchSWH2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 13.5
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
| Sun |  |  |  | Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  |  |  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 35.35
[5 empty] | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
[5 empty] | Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | SHW_Bath Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SHW_Bath Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SHW_Kitchen Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | SHW_Kitchen Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600